## Validasi
Date/Time | Zone Mean Air Temperature FILLING B [C] | Zone Air Relative Humidity FILLING B [%] | Chiller Electric Power CHILLER [W] | relative humidity measurement[%rH] | temperature clean room measurement[°C] | Site Outdoor Air Drybulb Temperature Environment [C] | Site Outdoor Air Relative Humidity Environment [%] | Date/Time | Zone Mean Air Temperature FILLING B [C] | Date/Time | Zone Air Relative Humidity FILLING B [%] | Date/Time | Chiller Electric Power CHILLER [W] | Tave EP | Rhave EP |  | RH meas | T meas
2021-06-03 | 23.182 | 42.0075 | 606.441 |  |  | 21.875 | 85.4167 | 2004-06-03 | 23.182 | 2004-06-03 | 42.0075 | 2004-06-03 | 606.441 | 23.6596 | 43.4428 | 657.8688 | 42.8454 | 24.2639
2021-06-03 00:05 | 23.1713 | 41.7258 | 604.957 |  |  | 21.85 | 85.8333 | 2004-06-03 00:05 | 23.1713 | 2004-06-03 00:05 | 41.7258 | 2004-06-03 00:05 | 604.957 |  |  |  | -0.59744 | 0.60436
2021-06-03 00:10 | 23.1614 | 41.4812 | 603.702 |  |  | 21.825 | 86.25 | 2004-06-03 00:10 | 23.1614 | 2004-06-03 00:10 | 41.4812 | 2004-06-03 00:10 | 603.702 |  |  |  | -1.394% | 2.491%
2021-06-03 00:15 | 23.1521 | 41.2694 | 602.646 |  |  | 21.8 | 86.6667 | 2004-06-03 00:15 | 23.1521 | 2004-06-03 00:15 | 41.2694 | 2004-06-03 00:15 | 602.646
2021-06-03 00:20 | 23.1433 | 41.0863 | 601.763 |  |  | 21.775 | 87.0833 | 2004-06-03 00:20 | 23.1433 | 2004-06-03 00:20 | 41.0863 | 2004-06-03 00:20 | 601.763
2021-06-03 00:25 | 23.1352 | 40.9283 | 601.034 |  |  | 21.75 | 87.5 | 2004-06-03 00:25 | 23.1352 | 2004-06-03 00:25 | 40.9283 | 2004-06-03 00:25 | 601.034
2021-06-03 00:30 | 23.1274 | 40.7924 | 600.438 |  |  | 21.725 | 87.9167 | 2004-06-03 00:30 | 23.1274 | 2004-06-03 00:30 | 40.7924 | 2004-06-03 00:30 | 600.438
2021-06-03 00:35 | 23.1201 | 40.6759 | 599.961 |  |  | 21.7 | 88.3333 | 2004-06-03 00:35 | 23.1201 | 2004-06-03 00:35 | 40.6759 | 2004-06-03 00:35 | 599.961
2021-06-03 00:40 | 23.1133 | 40.5764 | 599.587 |  |  | 21.675 | 88.75 | 2004-06-03 00:40 | 23.1133 | 2004-06-03 00:40 | 40.5764 | 2004-06-03 00:40 | 599.587
2021-06-03 00:45 | 23.1067 | 40.4917 | 599.305 |  |  | 21.65 | 89.1667 | 2004-06-03 00:45 | 23.1067 | 2004-06-03 00:45 | 40.4917 | 2004-06-03 00:45 | 599.305
2021-06-03 00:50 | 23.1005 | 40.42 | 599.102 |  |  | 21.625 | 89.5833 | 2004-06-03 00:50 | 23.1005 | 2004-06-03 00:50 | 40.42 | 2004-06-03 00:50 | 599.102
2021-06-03 00:55 | 23.0947 | 40.3597 | 598.97 |  |  | 21.6 | 90 | 2004-06-03 00:55 | 23.0947 | 2004-06-03 00:55 | 40.3597 | 2004-06-03 00:55 | 598.97
2021-06-03 01:00 | 23.0882 | 40.3103 | 598.354 |  |  | 21.6 | 89.8333 | 2004-06-03 01:00 | 23.0882 | 2004-06-03 01:00 | 40.3103 | 2004-06-03 01:00 | 598.354
2021-06-03 01:05 | 23.0817 | 40.2678 | 597.638 |  |  | 21.6 | 89.6667 | 2004-06-03 01:05 | 23.0817 | 2004-06-03 01:05 | 40.2678 | 2004-06-03 01:05 | 597.638
2021-06-03 01:10 | 23.0752 | 40.2312 | 596.951 |  |  | 21.6 | 89.5 | 2004-06-03 01:10 | 23.0752 | 2004-06-03 01:10 | 40.2312 | 2004-06-03 01:10 | 596.951
2021-06-03 01:15 | 23.0689 | 40.1996 | 596.294 |  |  | 21.6 | 89.3333 | 2004-06-03 01:15 | 23.0689 | 2004-06-03 01:15 | 40.1996 | 2004-06-03 01:15 | 596.294
2021-06-03 01:20 | 23.0627 | 40.1719 | 595.662 |  |  | 21.6 | 89.1667 | 2004-06-03 01:20 | 23.0627 | 2004-06-03 01:20 | 40.1719 | 2004-06-03 01:20 | 595.662
2021-06-03 01:25 | 23.0567 | 40.1479 | 595.056 |  |  | 21.6 | 89 | 2004-06-03 01:25 | 23.0567 | 2004-06-03 01:25 | 40.1479 | 2004-06-03 01:25 | 595.056
2021-06-03 01:30 | 23.0508 | 40.1272 | 594.472 |  |  | 21.6 | 88.8333 | 2004-06-03 01:30 | 23.0508 | 2004-06-03 01:30 | 40.1272 | 2004-06-03 01:30 | 594.472
2021-06-03 01:35 | 23.0451 | 40.1093 | 593.906 |  |  | 21.6 | 88.6667 | 2004-06-03 01:35 | 23.0451 | 2004-06-03 01:35 | 40.1093 | 2004-06-03 01:35 | 593.906
2021-06-03 01:40 | 23.0394 | 40.0937 | 593.358 |  |  | 21.6 | 88.5 | 2004-06-03 01:40 | 23.0394 | 2004-06-03 01:40 | 40.0937 | 2004-06-03 01:40 | 593.358
2021-06-03 01:45 | 23.0339 | 40.0803 | 592.825 |  |  | 21.6 | 88.3333 | 2004-06-03 01:45 | 23.0339 | 2004-06-03 01:45 | 40.0803 | 2004-06-03 01:45 | 592.825
2021-06-03 01:50 | 23.0285 | 40.0687 | 592.305 |  |  | 21.6 | 88.1667 | 2004-06-03 01:50 | 23.0285 | 2004-06-03 01:50 | 40.0687 | 2004-06-03 01:50 | 592.305
2021-06-03 01:55 | 23.0232 | 40.0587 | 591.796 |  |  | 21.6 | 88 | 2004-06-03 01:55 | 23.0232 | 2004-06-03 01:55 | 40.0587 | 2004-06-03 01:55 | 591.796
2021-06-03 02:00 | 23.0184 | 40.0506 | 591.583 |  |  | 21.5833 | 88.1667 | 2004-06-03 02:00 | 23.0184 | 2004-06-03 02:00 | 40.0506 | 2004-06-03 02:00 | 591.583
2021-06-03 02:05 | 23.0139 | 40.0446 | 591.46 |  |  | 21.5667 | 88.3333 | 2004-06-03 02:05 | 23.0139 | 2004-06-03 02:05 | 40.0446 | 2004-06-03 02:05 | 591.46
2021-06-03 02:10 | 23.0096 | 40.0406 | 591.356 |  |  | 21.55 | 88.5 | 2004-06-03 02:10 | 23.0096 | 2004-06-03 02:10 | 40.0406 | 2004-06-03 02:10 | 591.356
2021-06-03 02:15 | 23.0055 | 40.0383 | 591.266 |  |  | 21.5333 | 88.6667 | 2004-06-03 02:15 | 23.0055 | 2004-06-03 02:15 | 40.0383 | 2004-06-03 02:15 | 591.266
2021-06-03 02:20 | 23.0015 | 40.0376 | 591.189 |  |  | 21.5167 | 88.8333 | 2004-06-03 02:20 | 23.0015 | 2004-06-03 02:20 | 40.0376 | 2004-06-03 02:20 | 591.189
2021-06-03 02:25 | 22.9977 | 40.0383 | 591.123 |  |  | 21.5 | 89 | 2004-06-03 02:25 | 22.9977 | 2004-06-03 02:25 | 40.0383 | 2004-06-03 02:25 | 591.123
2021-06-03 02:30 | 22.9939 | 40.0402 | 591.066 |  |  | 21.4833 | 89.1667 | 2004-06-03 02:30 | 22.9939 | 2004-06-03 02:30 | 40.0402 | 2004-06-03 02:30 | 591.066
2021-06-03 02:35 | 22.9902 | 40.0431 | 591.017 |  |  | 21.4667 | 89.3333 | 2004-06-03 02:35 | 22.9902 | 2004-06-03 02:35 | 40.0431 | 2004-06-03 02:35 | 591.017
2021-06-03 02:40 | 22.9867 | 40.0469 | 590.975 |  |  | 21.45 | 89.5 | 2004-06-03 02:40 | 22.9867 | 2004-06-03 02:40 | 40.0469 | 2004-06-03 02:40 | 590.975
2021-06-03 02:45 | 22.9832 | 40.0516 | 590.94 |  |  | 21.4333 | 89.6667 | 2004-06-03 02:45 | 22.9832 | 2004-06-03 02:45 | 40.0516 | 2004-06-03 02:45 | 590.94
2021-06-03 02:50 | 22.9798 | 40.0569 | 590.911 |  |  | 21.4167 | 89.8333 | 2004-06-03 02:50 | 22.9798 | 2004-06-03 02:50 | 40.0569 | 2004-06-03 02:50 | 590.911
2021-06-03 02:55 | 22.9765 | 40.0627 | 590.886 |  |  | 21.4 | 90 | 2004-06-03 02:55 | 22.9765 | 2004-06-03 02:55 | 40.0627 | 2004-06-03 02:55 | 590.886
2021-06-03 03:00 | 22.9738 | 40.0698 | 591.362 |  |  | 21.3833 | 90.5 | 2004-06-03 03:00 | 22.9738 | 2004-06-03 03:00 | 40.0698 | 2004-06-03 03:00 | 591.362
2021-06-03 03:05 | 22.9715 | 40.0785 | 591.977 |  |  | 21.3667 | 91 | 2004-06-03 03:05 | 22.9715 | 2004-06-03 03:05 | 40.0785 | 2004-06-03 03:05 | 591.977
2021-06-03 03:10 | 22.9695 | 40.0888 | 592.61 |  |  | 21.35 | 91.5 | 2004-06-03 03:10 | 22.9695 | 2004-06-03 03:10 | 40.0888 | 2004-06-03 03:10 | 592.61
2021-06-03 03:15 | 22.9676 | 40.1007 | 593.257 |  |  | 21.3333 | 92 | 2004-06-03 03:15 | 22.9676 | 2004-06-03 03:15 | 40.1007 | 2004-06-03 03:15 | 593.257
2021-06-03 03:20 | 22.9658 | 40.114 | 593.913 |  |  | 21.3167 | 92.5 | 2004-06-03 03:20 | 22.9658 | 2004-06-03 03:20 | 40.114 | 2004-06-03 03:20 | 593.913
2021-06-03 03:25 | 22.9642 | 40.1285 | 594.578 |  |  | 21.3 | 93 | 2004-06-03 03:25 | 22.9642 | 2004-06-03 03:25 | 40.1285 | 2004-06-03 03:25 | 594.578
2021-06-03 03:30 | 22.9626 | 40.144 | 595.251 |  |  | 21.2833 | 93.5 | 2004-06-03 03:30 | 22.9626 | 2004-06-03 03:30 | 40.144 | 2004-06-03 03:30 | 595.251
2021-06-03 03:35 | 22.9611 | 40.1605 | 595.93 |  |  | 21.2667 | 94 | 2004-06-03 03:35 | 22.9611 | 2004-06-03 03:35 | 40.1605 | 2004-06-03 03:35 | 595.93
2021-06-03 03:40 | 22.9597 | 40.1777 | 596.614 |  |  | 21.25 | 94.5 | 2004-06-03 03:40 | 22.9597 | 2004-06-03 03:40 | 40.1777 | 2004-06-03 03:40 | 596.614
2021-06-03 03:45 | 22.9584 | 40.1957 | 597.303 |  |  | 21.2333 | 95 | 2004-06-03 03:45 | 22.9584 | 2004-06-03 03:45 | 40.1957 | 2004-06-03 03:45 | 597.303
2021-06-03 03:50 | 22.9572 | 40.2141 | 597.995 |  |  | 21.2167 | 95.5 | 2004-06-03 03:50 | 22.9572 | 2004-06-03 03:50 | 40.2141 | 2004-06-03 03:50 | 597.995
2021-06-03 03:55 | 22.956 | 40.2331 | 598.691 |  |  | 21.2 | 96 | 2004-06-03 03:55 | 22.956 | 2004-06-03 03:55 | 40.2331 | 2004-06-03 03:55 | 598.691
2021-06-03 04:00 | 22.9536 | 40.2508 | 598.285 |  |  | 21.1833 | 95.75 | 2004-06-03 04:00 | 22.9536 | 2004-06-03 04:00 | 40.2508 | 2004-06-03 04:00 | 598.285
2021-06-03 04:05 | 22.9505 | 40.2662 | 597.577 |  |  | 21.1667 | 95.5 | 2004-06-03 04:05 | 22.9505 | 2004-06-03 04:05 | 40.2662 | 2004-06-03 04:05 | 597.577
2021-06-03 04:10 | 22.9472 | 40.2789 | 596.841 |  |  | 21.15 | 95.25 | 2004-06-03 04:10 | 22.9472 | 2004-06-03 04:10 | 40.2789 | 2004-06-03 04:10 | 596.841
2021-06-03 04:15 | 22.9437 | 40.2891 | 596.084 |  |  | 21.1333 | 95 | 2004-06-03 04:15 | 22.9437 | 2004-06-03 04:15 | 40.2891 | 2004-06-03 04:15 | 596.084
2021-06-03 04:20 | 22.9402 | 40.297 | 595.311 |  |  | 21.1167 | 94.75 | 2004-06-03 04:20 | 22.9402 | 2004-06-03 04:20 | 40.297 | 2004-06-03 04:20 | 595.311
2021-06-03 04:25 | 22.9366 | 40.3027 | 594.526 |  |  | 21.1 | 94.5 | 2004-06-03 04:25 | 22.9366 | 2004-06-03 04:25 | 40.3027 | 2004-06-03 04:25 | 594.526
2021-06-03 04:30 | 22.9329 | 40.3066 | 593.73 |  |  | 21.0833 | 94.25 | 2004-06-03 04:30 | 22.9329 | 2004-06-03 04:30 | 40.3066 | 2004-06-03 04:30 | 593.73
2021-06-03 04:35 | 22.9293 | 40.3088 | 592.925 |  |  | 21.0667 | 94 | 2004-06-03 04:35 | 22.9293 | 2004-06-03 04:35 | 40.3088 | 2004-06-03 04:35 | 592.925
2021-06-03 04:40 | 22.9256 | 40.3094 | 592.112 |  |  | 21.05 | 93.75 | 2004-06-03 04:40 | 22.9256 | 2004-06-03 04:40 | 40.3094 | 2004-06-03 04:40 | 592.112
2021-06-03 04:45 | 22.9219 | 40.3088 | 591.292 |  |  | 21.0333 | 93.5 | 2004-06-03 04:45 | 22.9219 | 2004-06-03 04:45 | 40.3088 | 2004-06-03 04:45 | 591.292
2021-06-03 04:50 | 22.9182 | 40.3071 | 590.467 |  |  | 21.0167 | 93.25 | 2004-06-03 04:50 | 22.9182 | 2004-06-03 04:50 | 40.3071 | 2004-06-03 04:50 | 590.467
2021-06-03 04:55 | 22.9145 | 40.3044 | 589.637 |  |  | 21 | 93 | 2004-06-03 04:55 | 22.9145 | 2004-06-03 04:55 | 40.3044 | 2004-06-03 04:55 | 589.637
2021-06-03 05:00 | 22.9119 | 40.302 | 589.75 |  |  | 21 | 93.25 | 2004-06-03 05:00 | 22.9119 | 2004-06-03 05:00 | 40.302 | 2004-06-03 05:00 | 589.75
2021-06-03 05:05 | 22.9098 | 40.301 | 590.119 |  |  | 21 | 93.5 | 2004-06-03 05:05 | 22.9098 | 2004-06-03 05:05 | 40.301 | 2004-06-03 05:05 | 590.119
2021-06-03 05:10 | 22.908 | 40.3017 | 590.511 |  |  | 21 | 93.75 | 2004-06-03 05:10 | 22.908 | 2004-06-03 05:10 | 40.3017 | 2004-06-03 05:10 | 590.511
2021-06-03 05:15 | 22.9063 | 40.304 | 590.919 |  |  | 21 | 94 | 2004-06-03 05:15 | 22.9063 | 2004-06-03 05:15 | 40.304 | 2004-06-03 05:15 | 590.919
2021-06-03 05:20 | 22.9048 | 40.3078 | 591.34 |  |  | 21 | 94.25 | 2004-06-03 05:20 | 22.9048 | 2004-06-03 05:20 | 40.3078 | 2004-06-03 05:20 | 591.34
2021-06-03 05:25 | 22.9034 | 40.313 | 591.772 |  |  | 21 | 94.5 | 2004-06-03 05:25 | 22.9034 | 2004-06-03 05:25 | 40.313 | 2004-06-03 05:25 | 591.772
2021-06-03 05:30 | 22.902 | 40.3193 | 592.213 |  |  | 21 | 94.75 | 2004-06-03 05:30 | 22.902 | 2004-06-03 05:30 | 40.3193 | 2004-06-03 05:30 | 592.213
2021-06-03 05:35 | 22.9007 | 40.3268 | 592.662 |  |  | 21 | 95 | 2004-06-03 05:35 | 22.9007 | 2004-06-03 05:35 | 40.3268 | 2004-06-03 05:35 | 592.662
2021-06-03 05:40 | 22.8994 | 40.3351 | 593.117 |  |  | 21 | 95.25 | 2004-06-03 05:40 | 22.8994 | 2004-06-03 05:40 | 40.3351 | 2004-06-03 05:40 | 593.117
2021-06-03 05:45 | 22.8982 | 40.3443 | 593.579 |  |  | 21 | 95.5 | 2004-06-03 05:45 | 22.8982 | 2004-06-03 05:45 | 40.3443 | 2004-06-03 05:45 | 593.579
2021-06-03 05:50 | 22.8971 | 40.3541 | 594.047 |  |  | 21 | 95.75 | 2004-06-03 05:50 | 22.8971 | 2004-06-03 05:50 | 40.3541 | 2004-06-03 05:50 | 594.047
2021-06-03 05:55 | 22.896 | 40.3646 | 594.518 |  |  | 21 | 96 | 2004-06-03 05:55 | 22.896 | 2004-06-03 05:55 | 40.3646 | 2004-06-03 05:55 | 594.518
2021-06-03 06:00 | 22.8949 | 40.3755 | 595.079 |  |  | 21.0333 | 96 | 2004-06-03 06:00 | 22.8949 | 2004-06-03 06:00 | 40.3755 | 2004-06-03 06:00 | 595.079
2021-06-03 06:05 | 22.8938 | 40.3867 | 595.664 |  |  | 21.0667 | 96 | 2004-06-03 06:05 | 22.8938 | 2004-06-03 06:05 | 40.3867 | 2004-06-03 06:05 | 595.664
2021-06-03 06:10 | 22.8928 | 40.3982 | 596.251 |  |  | 21.1 | 96 | 2004-06-03 06:10 | 22.8928 | 2004-06-03 06:10 | 40.3982 | 2004-06-03 06:10 | 596.251
2021-06-03 06:15 | 22.8918 | 40.4099 | 596.841 |  |  | 21.1333 | 96 | 2004-06-03 06:15 | 22.8918 | 2004-06-03 06:15 | 40.4099 | 2004-06-03 06:15 | 596.841
2021-06-03 06:20 | 22.8908 | 40.4217 | 597.433 |  |  | 21.1667 | 96 | 2004-06-03 06:20 | 22.8908 | 2004-06-03 06:20 | 40.4217 | 2004-06-03 06:20 | 597.433
2021-06-03 06:25 | 22.8899 | 40.4337 | 598.028 |  |  | 21.2 | 96 | 2004-06-03 06:25 | 22.8899 | 2004-06-03 06:25 | 40.4337 | 2004-06-03 06:25 | 598.028
2021-06-03 06:30 | 22.889 | 40.4458 | 598.625 |  |  | 21.2333 | 96 | 2004-06-03 06:30 | 22.889 | 2004-06-03 06:30 | 40.4458 | 2004-06-03 06:30 | 598.625
2021-06-03 06:35 | 22.8881 | 40.458 | 599.224 |  |  | 21.2667 | 96 | 2004-06-03 06:35 | 22.8881 | 2004-06-03 06:35 | 40.458 | 2004-06-03 06:35 | 599.224
2021-06-03 06:40 | 22.8872 | 40.4703 | 599.825 |  |  | 21.3 | 96 | 2004-06-03 06:40 | 22.8872 | 2004-06-03 06:40 | 40.4703 | 2004-06-03 06:40 | 599.825
2021-06-03 06:45 | 22.8864 | 40.4827 | 600.428 |  |  | 21.3333 | 96 | 2004-06-03 06:45 | 22.8864 | 2004-06-03 06:45 | 40.4827 | 2004-06-03 06:45 | 600.428
2021-06-03 06:50 | 22.8856 | 40.4952 | 601.032 |  |  | 21.3667 | 96 | 2004-06-03 06:50 | 22.8856 | 2004-06-03 06:50 | 40.4952 | 2004-06-03 06:50 | 601.032
2021-06-03 06:55 | 22.8849 | 40.5076 | 601.638 |  |  | 21.4 | 96 | 2004-06-03 06:55 | 22.8849 | 2004-06-03 06:55 | 40.5076 | 2004-06-03 06:55 | 601.638
2021-06-03 07:00 | 22.8837 | 40.5196 | 601.963 |  |  | 21.4583 | 95.5833 | 2004-06-03 07:00 | 22.8837 | 2004-06-03 07:00 | 40.5196 | 2004-06-03 07:00 | 601.963
2021-06-03 07:05 | 22.8823 | 40.5306 | 602.204 |  |  | 21.5167 | 95.1667 | 2004-06-03 07:05 | 22.8823 | 2004-06-03 07:05 | 40.5306 | 2004-06-03 07:05 | 602.204
2021-06-03 07:10 | 22.8808 | 40.5406 | 602.432 |  |  | 21.575 | 94.75 | 2004-06-03 07:10 | 22.8808 | 2004-06-03 07:10 | 40.5406 | 2004-06-03 07:10 | 602.432
2021-06-03 07:15 | 22.8793 | 40.5496 | 602.648 |  |  | 21.6333 | 94.3333 | 2004-06-03 07:15 | 22.8793 | 2004-06-03 07:15 | 40.5496 | 2004-06-03 07:15 | 602.648
2021-06-03 07:20 | 22.8778 | 40.5577 | 602.854 |  |  | 21.6917 | 93.9167 | 2004-06-03 07:20 | 22.8778 | 2004-06-03 07:20 | 40.5577 | 2004-06-03 07:20 | 602.854
2021-06-03 07:25 | 22.8762 | 40.565 | 603.051 |  |  | 21.75 | 93.5 | 2004-06-03 07:25 | 22.8762 | 2004-06-03 07:25 | 40.565 | 2004-06-03 07:25 | 603.051
2021-06-03 07:30 | 22.8746 | 40.5715 | 603.239 |  |  | 21.8083 | 93.0833 | 2004-06-03 07:30 | 22.8746 | 2004-06-03 07:30 | 40.5715 | 2004-06-03 07:30 | 603.239
2021-06-03 07:35 | 22.873 | 40.5774 | 603.421 |  |  | 21.8667 | 92.6667 | 2004-06-03 07:35 | 22.873 | 2004-06-03 07:35 | 40.5774 | 2004-06-03 07:35 | 603.421
2021-06-03 07:40 | 22.8713 | 40.5826 | 603.594 |  |  | 21.925 | 92.25 | 2004-06-03 07:40 | 22.8713 | 2004-06-03 07:40 | 40.5826 | 2004-06-03 07:40 | 603.594
2021-06-03 07:45 | 22.8697 | 40.5873 | 603.761 |  |  | 21.9833 | 91.8333 | 2004-06-03 07:45 | 22.8697 | 2004-06-03 07:45 | 40.5873 | 2004-06-03 07:45 | 603.761
2021-06-03 07:50 | 22.8681 | 40.5914 | 603.922 |  |  | 22.0417 | 91.4167 | 2004-06-03 07:50 | 22.8681 | 2004-06-03 07:50 | 40.5914 | 2004-06-03 07:50 | 603.922
2021-06-03 07:55 | 22.8664 | 40.5952 | 604.076 |  |  | 22.1 | 91 | 2004-06-03 07:55 | 22.8664 | 2004-06-03 07:55 | 40.5952 | 2004-06-03 07:55 | 604.076
2021-06-03 08:00 | 22.8657 | 40.5995 | 604.986 |  |  | 22.1667 | 91 | 2004-06-03 08:00 | 22.8657 | 2004-06-03 08:00 | 40.5995 | 2004-06-03 08:00 | 604.986
2021-06-03 08:05 | 22.8654 | 40.6053 | 606.106 |  |  | 22.2333 | 91 | 2004-06-03 08:05 | 22.8654 | 2004-06-03 08:05 | 40.6053 | 2004-06-03 08:05 | 606.106
2021-06-03 08:10 | 22.8653 | 40.6127 | 607.249 |  |  | 22.3 | 91 | 2004-06-03 08:10 | 22.8653 | 2004-06-03 08:10 | 40.6127 | 2004-06-03 08:10 | 607.249
2021-06-03 08:15 | 22.8654 | 40.6217 | 608.409 |  |  | 22.3667 | 91 | 2004-06-03 08:15 | 22.8654 | 2004-06-03 08:15 | 40.6217 | 2004-06-03 08:15 | 608.409
2021-06-03 08:20 | 22.8656 | 40.6321 | 609.583 |  |  | 22.4333 | 91 | 2004-06-03 08:20 | 22.8656 | 2004-06-03 08:20 | 40.6321 | 2004-06-03 08:20 | 609.583
2021-06-03 08:25 | 22.8659 | 40.6439 | 610.77 |  |  | 22.5 | 91 | 2004-06-03 08:25 | 22.8659 | 2004-06-03 08:25 | 40.6439 | 2004-06-03 08:25 | 610.77
2021-06-03 08:30 | 22.8662 | 40.6568 | 611.967 |  |  | 22.5667 | 91 | 2004-06-03 08:30 | 22.8662 | 2004-06-03 08:30 | 40.6568 | 2004-06-03 08:30 | 611.967
2021-06-03 08:35 | 22.8666 | 40.6707 | 613.175 |  |  | 22.6333 | 91 | 2004-06-03 08:35 | 22.8666 | 2004-06-03 08:35 | 40.6707 | 2004-06-03 08:35 | 613.175
2021-06-03 08:40 | 22.8671 | 40.6856 | 614.392 |  |  | 22.7 | 91 | 2004-06-03 08:40 | 22.8671 | 2004-06-03 08:40 | 40.6856 | 2004-06-03 08:40 | 614.392
2021-06-03 08:45 | 22.8677 | 40.7012 | 615.617 | 40 | 24.9 | 22.7667 | 91 | 2004-06-03 08:45 | 22.8677 | 2004-06-03 08:45 | 40.7012 | 2004-06-03 08:45 | 615.617
2021-06-03 08:50 | 22.8683 | 40.7175 | 616.85 | 41.3 | 24.3 | 22.8333 | 91 | 2004-06-03 08:50 | 22.8683 | 2004-06-03 08:50 | 40.7175 | 2004-06-03 08:50 | 616.85
2021-06-03 08:55 | 22.8689 | 40.7344 | 618.091 | 40.9 | 24.4 | 22.9 | 91 | 2004-06-03 08:55 | 22.8689 | 2004-06-03 08:55 | 40.7344 | 2004-06-03 08:55 | 618.091
2021-06-03 09:00 | 22.868 | 40.7499 | 618.066 | 40.9 | 24.2 | 22.9833 | 90.0833 | 2004-06-03 09:00 | 22.868 | 2004-06-03 09:00 | 40.7499 | 2004-06-03 09:00 | 618.066
2021-06-03 09:05 | 22.8664 | 40.7625 | 617.68 | 40.1 | 23.9 | 23.0667 | 89.1667 | 2004-06-03 09:05 | 22.8664 | 2004-06-03 09:05 | 40.7625 | 2004-06-03 09:05 | 617.68
2021-06-03 09:10 | 22.8643 | 40.7719 | 617.242 | 39.6 | 23.9 | 23.15 | 88.25 | 2004-06-03 09:10 | 22.8643 | 2004-06-03 09:10 | 40.7719 | 2004-06-03 09:10 | 617.242
2021-06-03 09:15 | 22.862 | 40.7781 | 616.762 | 39.8 | 23.9 | 23.2333 | 87.3333 | 2004-06-03 09:15 | 22.862 | 2004-06-03 09:15 | 40.7781 | 2004-06-03 09:15 | 616.762
2021-06-03 09:20 | 22.8595 | 40.7814 | 616.246 | 39.5 | 23.9 | 23.3167 | 86.4167 | 2004-06-03 09:20 | 22.8595 | 2004-06-03 09:20 | 40.7814 | 2004-06-03 09:20 | 616.246
2021-06-03 09:25 | 22.857 | 40.7819 | 615.697 | 40 | 23.8 | 23.4 | 85.5 | 2004-06-03 09:25 | 22.857 | 2004-06-03 09:25 | 40.7819 | 2004-06-03 09:25 | 615.697
2021-06-03 09:30 | 22.8543 | 40.7799 | 615.116 | 40 | 23.9 | 23.4833 | 84.5833 | 2004-06-03 09:30 | 22.8543 | 2004-06-03 09:30 | 40.7799 | 2004-06-03 09:30 | 615.116
2021-06-03 09:35 | 22.8517 | 40.7754 | 614.507 | 40.3 | 23.9 | 23.5667 | 83.6667 | 2004-06-03 09:35 | 22.8517 | 2004-06-03 09:35 | 40.7754 | 2004-06-03 09:35 | 614.507
2021-06-03 09:40 | 22.8489 | 40.7691 | 613.871 | 40.3 | 23.9 | 23.65 | 82.75 | 2004-06-03 09:40 | 22.8489 | 2004-06-03 09:40 | 40.7691 | 2004-06-03 09:40 | 613.871
2021-06-03 09:45 | 22.8461 | 40.7608 | 613.207 | 40.8 | 23.8 | 23.7333 | 81.8333 | 2004-06-03 09:45 | 22.8461 | 2004-06-03 09:45 | 40.7608 | 2004-06-03 09:45 | 613.207
2021-06-03 09:50 | 22.8432 | 40.7507 | 612.519 | 40.8 | 23.8 | 23.8167 | 80.9167 | 2004-06-03 09:50 | 22.8432 | 2004-06-03 09:50 | 40.7507 | 2004-06-03 09:50 | 612.519
2021-06-03 09:55 | 22.8402 | 40.7394 | 611.806 | 41 | 23.8 | 23.9 | 80 | 2004-06-03 09:55 | 22.8402 | 2004-06-03 09:55 | 40.7394 | 2004-06-03 09:55 | 611.806
2021-06-03 10:00 | 23.0531 | 40.2015 | 611.86 | 40.6 | 23.9 | 23.9667 | 79.6667 | 2004-06-03 10:00 | 23.0531 | 2004-06-03 10:00 | 40.2015 | 2004-06-03 10:00 | 611.86
2021-06-03 10:05 | 23.1558 | 39.9404 | 614.852 | 40.6 | 23.9 | 24.0333 | 79.3333 | 2004-06-03 10:05 | 23.1558 | 2004-06-03 10:05 | 39.9404 | 2004-06-03 10:05 | 614.852
2021-06-03 10:10 | 23.2104 | 39.7989 | 617.581 | 40.5 | 24 | 24.1 | 79 | 2004-06-03 10:10 | 23.2104 | 2004-06-03 10:10 | 39.7989 | 2004-06-03 10:10 | 617.581
2021-06-03 10:15 | 23.2411 | 39.7171 | 619.495 | 40.7 | 24 | 24.1667 | 78.6667 | 2004-06-03 10:15 | 23.2411 | 2004-06-03 10:15 | 39.7171 | 2004-06-03 10:15 | 619.495
2021-06-03 10:20 | 23.2602 | 39.6646 | 621.017 | 40.6 | 24 | 24.2333 | 78.3333 | 2004-06-03 10:20 | 23.2602 | 2004-06-03 10:20 | 39.6646 | 2004-06-03 10:20 | 621.017
2021-06-03 10:25 | 23.2733 | 39.6274 | 622.349 | 40.5 | 24.1 | 24.3 | 78 | 2004-06-03 10:25 | 23.2733 | 2004-06-03 10:25 | 39.6274 | 2004-06-03 10:25 | 622.349
2021-06-03 10:30 | 23.2832 | 39.5988 | 623.587 | 40.1 | 24.1 | 24.3667 | 77.6667 | 2004-06-03 10:30 | 23.2832 | 2004-06-03 10:30 | 39.5988 | 2004-06-03 10:30 | 623.587
2021-06-03 10:35 | 23.2913 | 39.5754 | 624.775 | 40.2 | 24.2 | 24.4333 | 77.3333 | 2004-06-03 10:35 | 23.2913 | 2004-06-03 10:35 | 39.5754 | 2004-06-03 10:35 | 624.775
2021-06-03 10:40 | 23.2983 | 39.5552 | 625.936 | 40.1 | 24.2 | 24.5 | 77 | 2004-06-03 10:40 | 23.2983 | 2004-06-03 10:40 | 39.5552 | 2004-06-03 10:40 | 625.936
2021-06-03 10:45 | 23.3045 | 39.5372 | 627.081 | 39.7 | 24.2 | 24.5667 | 76.6667 | 2004-06-03 10:45 | 23.3045 | 2004-06-03 10:45 | 39.5372 | 2004-06-03 10:45 | 627.081
2021-06-03 10:50 | 23.3101 | 39.5211 | 628.216 | 40 | 24.4 | 24.6333 | 76.3333 | 2004-06-03 10:50 | 23.3101 | 2004-06-03 10:50 | 39.5211 | 2004-06-03 10:50 | 628.216
2021-06-03 10:55 | 23.4915 | 39.8496 | 629.344 | 39.8 | 24.5 | 24.7 | 76 | 2004-06-03 10:55 | 23.4915 | 2004-06-03 10:55 | 39.8496 | 2004-06-03 10:55 | 629.344
2021-06-03 11:00 | 23.5631 | 39.7605 | 636.939 | 39.9 | 24.6 | 24.75 | 76.75 | 2004-06-03 11:00 | 23.5631 | 2004-06-03 11:00 | 39.7605 | 2004-06-03 11:00 | 636.939
2021-06-03 11:05 | 23.6085 | 39.7348 | 642.374 | 39.4 | 24.8 | 24.8 | 77.5 | 2004-06-03 11:05 | 23.6085 | 2004-06-03 11:05 | 39.7348 | 2004-06-03 11:05 | 642.374
2021-06-03 11:10 | 23.6404 | 39.7413 | 646.609 | 39.6 | 24.7 | 24.85 | 78.25 | 2004-06-03 11:10 | 23.6404 | 2004-06-03 11:10 | 39.7413 | 2004-06-03 11:10 | 646.609
2021-06-03 11:15 | 23.665 | 39.764 | 650.63 | 39.5 | 24.6 | 24.9 | 79 | 2004-06-03 11:15 | 23.665 | 2004-06-03 11:15 | 39.764 | 2004-06-03 11:15 | 650.63
2021-06-03 11:20 | 23.6857 | 39.7949 | 654.546 | 39.4 | 24.7 | 24.95 | 79.75 | 2004-06-03 11:20 | 23.6857 | 2004-06-03 11:20 | 39.7949 | 2004-06-03 11:20 | 654.546
2021-06-03 11:25 | 23.7042 | 39.8301 | 658.412 | 39.2 | 24.8 | 25 | 80.5 | 2004-06-03 11:25 | 23.7042 | 2004-06-03 11:25 | 39.8301 | 2004-06-03 11:25 | 658.412
2021-06-03 11:30 | 23.7214 | 39.8674 | 662.255 | 39.3 | 24.7 | 25.05 | 81.25 | 2004-06-03 11:30 | 23.7214 | 2004-06-03 11:30 | 39.8674 | 2004-06-03 11:30 | 662.255
2021-06-03 11:35 | 23.7377 | 39.9061 | 666.091 | 39.4 | 24.8 | 25.1 | 82 | 2004-06-03 11:35 | 23.7377 | 2004-06-03 11:35 | 39.9061 | 2004-06-03 11:35 | 666.091
2021-06-03 11:40 | 23.7534 | 39.9455 | 669.927 | 39.4 | 24.8 | 25.15 | 82.75 | 2004-06-03 11:40 | 23.7534 | 2004-06-03 11:40 | 39.9455 | 2004-06-03 11:40 | 669.927
2021-06-03 11:45 | 23.7687 | 39.9853 | 673.768 | 39.4 | 24.8 | 25.2 | 83.5 | 2004-06-03 11:45 | 23.7687 | 2004-06-03 11:45 | 39.9853 | 2004-06-03 11:45 | 673.768
2021-06-03 11:50 | 23.7835 | 40.0255 | 677.618 | 39.4 | 24.9 | 25.25 | 84.25 | 2004-06-03 11:50 | 23.7835 | 2004-06-03 11:50 | 40.0255 | 2004-06-03 11:50 | 677.618
2021-06-03 11:55 | 23.798 | 40.066 | 681.478 | 39.5 | 24.8 | 25.3 | 85 | 2004-06-03 11:55 | 23.798 | 2004-06-03 11:55 | 40.066 | 2004-06-03 11:55 | 681.478
2021-06-03 12:00 | 23.7531 | 40.175 | 683.952 | 39.6 | 24.8 | 25.3333 | 85.25 | 2004-06-03 12:00 | 23.7531 | 2004-06-03 12:00 | 40.175 | 2004-06-03 12:00 | 683.952
2021-06-03 12:05 | 23.7344 | 40.2228 | 685.18 | 39.4 | 24.9 | 25.3667 | 85.5 | 2004-06-03 12:05 | 23.7344 | 2004-06-03 12:05 | 40.2228 | 2004-06-03 12:05 | 685.18
2021-06-03 12:10 | 23.7284 | 40.2428 | 686.475 | 39.4 | 24.9 | 25.4 | 85.75 | 2004-06-03 12:10 | 23.7284 | 2004-06-03 12:10 | 40.2428 | 2004-06-03 12:10 | 686.475
2021-06-03 12:15 | 23.7287 | 40.2501 | 687.997 | 39.7 | 24.8 | 25.4333 | 86 | 2004-06-03 12:15 | 23.7287 | 2004-06-03 12:15 | 40.2501 | 2004-06-03 12:15 | 687.997
2021-06-03 12:20 | 23.7322 | 40.2524 | 689.643 | 39.7 | 24.9 | 25.4667 | 86.25 | 2004-06-03 12:20 | 23.7322 | 2004-06-03 12:20 | 40.2524 | 2004-06-03 12:20 | 689.643
2021-06-03 12:25 | 23.7373 | 40.2533 | 691.359 | 39.3 | 25.1 | 25.5 | 86.5 | 2004-06-03 12:25 | 23.7373 | 2004-06-03 12:25 | 40.2533 | 2004-06-03 12:25 | 691.359
2021-06-03 12:30 | 23.744 | 40.2826 | 693.118 | 39.5 | 25 | 25.5333 | 86.75 | 2004-06-03 12:30 | 23.744 | 2004-06-03 12:30 | 40.2826 | 2004-06-03 12:30 | 693.118
2021-06-03 12:35 | 23.7509 | 40.3099 | 694.907 | 40 | 24.9 | 25.5667 | 87 | 2004-06-03 12:35 | 23.7509 | 2004-06-03 12:35 | 40.3099 | 2004-06-03 12:35 | 694.907
2021-06-03 12:40 | 23.7579 | 40.3356 | 696.717 | 40.3 | 24.9 | 25.6 | 87.25 | 2004-06-03 12:40 | 23.7579 | 2004-06-03 12:40 | 40.3356 | 2004-06-03 12:40 | 696.717
2021-06-03 12:45 | 23.765 | 40.36 | 698.544 | 40.5 | 24.9 | 25.6333 | 87.5 | 2004-06-03 12:45 | 23.765 | 2004-06-03 12:45 | 40.36 | 2004-06-03 12:45 | 698.544
2021-06-03 12:50 | 23.7722 | 40.3832 | 700.387 | 40.4 | 25 | 25.6667 | 87.75 | 2004-06-03 12:50 | 23.7722 | 2004-06-03 12:50 | 40.3832 | 2004-06-03 12:50 | 700.387
2021-06-03 12:55 | 23.7793 | 40.4055 | 702.242 | 40.3 | 25 | 25.7 | 88 | 2004-06-03 12:55 | 23.7793 | 2004-06-03 12:55 | 40.4055 | 2004-06-03 12:55 | 702.242
2021-06-03 13:00 | 23.7832 | 40.4233 | 701.549 | 40.4 | 24.8 | 25.7417 | 86.8333 | 2004-06-03 13:00 | 23.7832 | 2004-06-03 13:00 | 40.4233 | 2004-06-03 13:00 | 701.549
2021-06-03 13:05 | 23.7853 | 40.4335 | 700.11 | 40.1 | 24.9 | 25.7833 | 85.6667 | 2004-06-03 13:05 | 23.7853 | 2004-06-03 13:05 | 40.4335 | 2004-06-03 13:05 | 700.11
2021-06-03 13:10 | 23.7864 | 40.4359 | 698.575 | 40.2 | 24.8 | 25.825 | 84.5 | 2004-06-03 13:10 | 23.7864 | 2004-06-03 13:10 | 40.4359 | 2004-06-03 13:10 | 698.575
2021-06-03 13:15 | 23.7869 | 40.4306 | 696.966 | 40.3 | 24.9 | 25.8667 | 83.3333 | 2004-06-03 13:15 | 23.7869 | 2004-06-03 13:15 | 40.4306 | 2004-06-03 13:15 | 696.966
2021-06-03 13:20 | 23.787 | 40.4182 | 695.294 | 40.6 | 24.9 | 25.9083 | 82.1667 | 2004-06-03 13:20 | 23.787 | 2004-06-03 13:20 | 40.4182 | 2004-06-03 13:20 | 695.294
2021-06-03 13:25 | 23.7868 | 40.3995 | 693.567 | 40.5 | 24.9 | 25.95 | 81 | 2004-06-03 13:25 | 23.7868 | 2004-06-03 13:25 | 40.3995 | 2004-06-03 13:25 | 693.567
2021-06-03 13:30 | 23.7854 | 40.3502 | 691.79 | 40.6 | 24.9 | 25.9917 | 79.8333 | 2004-06-03 13:30 | 23.7854 | 2004-06-03 13:30 | 40.3502 | 2004-06-03 13:30 | 691.79
2021-06-03 13:35 | 23.7841 | 40.2988 | 689.967 | 40.8 | 25 | 26.0333 | 78.6667 | 2004-06-03 13:35 | 23.7841 | 2004-06-03 13:35 | 40.2988 | 2004-06-03 13:35 | 689.967
2021-06-03 13:40 | 23.7828 | 40.246 | 688.102 | 40.8 | 25 | 26.075 | 77.5 | 2004-06-03 13:40 | 23.7828 | 2004-06-03 13:40 | 40.246 | 2004-06-03 13:40 | 688.102
2021-06-03 13:45 | 23.7814 | 40.1919 | 686.197 | 40.9 | 25 | 26.1167 | 76.3333 | 2004-06-03 13:45 | 23.7814 | 2004-06-03 13:45 | 40.1919 | 2004-06-03 13:45 | 686.197
2021-06-03 13:50 | 23.7799 | 40.1368 | 684.255 | 41 | 25.1 | 26.1583 | 75.1667 | 2004-06-03 13:50 | 23.7799 | 2004-06-03 13:50 | 40.1368 | 2004-06-03 13:50 | 684.255
2021-06-03 13:55 | 23.7783 | 40.0807 | 682.279 | 40.5 | 25.1 | 26.2 | 74 | 2004-06-03 13:55 | 23.7783 | 2004-06-03 13:55 | 40.0807 | 2004-06-03 13:55 | 682.279
2021-06-03 14:00 | 23.7842 | 40.1927 | 680.385 | 40.5 | 25 | 26.2 | 73.4167 | 2004-06-03 14:00 | 23.7842 | 2004-06-03 14:00 | 40.1927 | 2004-06-03 14:00 | 680.385
2021-06-03 14:05 | 23.7881 | 40.2893 | 679.457 | 40.5 | 25.1 | 26.2 | 72.8333 | 2004-06-03 14:05 | 23.7881 | 2004-06-03 14:05 | 40.2893 | 2004-06-03 14:05 | 679.457
2021-06-03 14:10 | 23.7909 | 40.3706 | 678.623 | 40.6 | 25.2 | 26.2 | 72.25 | 2004-06-03 14:10 | 23.7909 | 2004-06-03 14:10 | 40.3706 | 2004-06-03 14:10 | 678.623
2021-06-03 14:15 | 23.7931 | 40.4376 | 677.677 | 39.4 | 25.1 | 26.2 | 71.6667 | 2004-06-03 14:15 | 23.7931 | 2004-06-03 14:15 | 40.4376 | 2004-06-03 14:15 | 677.677
2021-06-03 14:20 | 23.795 | 40.4918 | 676.638 | 39.2 | 25 | 26.2 | 71.0833 | 2004-06-03 14:20 | 23.795 | 2004-06-03 14:20 | 40.4918 | 2004-06-03 14:20 | 676.638
2021-06-03 14:25 | 23.7965 | 40.5345 | 675.517 | 39 | 25 | 26.2 | 70.5 | 2004-06-03 14:25 | 23.7965 | 2004-06-03 14:25 | 40.5345 | 2004-06-03 14:25 | 675.517
2021-06-03 14:30 | 23.7979 | 40.567 | 674.328 | 38.7 | 25 | 26.2 | 69.9167 | 2004-06-03 14:30 | 23.7979 | 2004-06-03 14:30 | 40.567 | 2004-06-03 14:30 | 674.328
2021-06-03 14:35 | 23.799 | 40.5907 | 673.079 | 38.6 | 25 | 26.2 | 69.3333 | 2004-06-03 14:35 | 23.799 | 2004-06-03 14:35 | 40.5907 | 2004-06-03 14:35 | 673.079
2021-06-03 14:40 | 23.8001 | 40.6064 | 671.776 | 38.6 | 24.9 | 26.2 | 68.75 | 2004-06-03 14:40 | 23.8001 | 2004-06-03 14:40 | 40.6064 | 2004-06-03 14:40 | 671.776
2021-06-03 14:45 | 23.801 | 40.6153 | 670.427 | 38.5 | 24.9 | 26.2 | 68.1667 | 2004-06-03 14:45 | 23.801 | 2004-06-03 14:45 | 40.6153 | 2004-06-03 14:45 | 670.427
2021-06-03 14:50 | 23.8018 | 40.6182 | 669.037 | 38.6 | 24.8 | 26.2 | 67.5833 | 2004-06-03 14:50 | 23.8018 | 2004-06-03 14:50 | 40.6182 | 2004-06-03 14:50 | 669.037
2021-06-03 14:55 | 23.8024 | 40.6158 | 667.611 | 39.3 | 24.8 | 26.2 | 67 | 2004-06-03 14:55 | 23.8024 | 2004-06-03 14:55 | 40.6158 | 2004-06-03 14:55 | 667.611
2021-06-03 15:00 | 23.5848 | 41.15 | 666.718 | 38.7 | 24.8 | 26.175 | 67 | 2004-06-03 15:00 | 23.5848 | 2004-06-03 15:00 | 41.15 | 2004-06-03 15:00 | 666.718
2021-06-03 15:05 | 23.4824 | 41.3957 | 663.517 | 39.3 | 24.8 | 26.15 | 67 | 2004-06-03 15:05 | 23.4824 | 2004-06-03 15:05 | 41.3957 | 2004-06-03 15:05 | 663.517
2021-06-03 15:10 | 23.4305 | 41.5133 | 660.991 | 39.4 | 24.7 | 26.125 | 67 | 2004-06-03 15:10 | 23.4305 | 2004-06-03 15:10 | 41.5133 | 2004-06-03 15:10 | 660.991
2021-06-03 15:15 | 23.4031 | 41.569 | 659.35 | 40.4 | 24.5 | 26.1 | 67 | 2004-06-03 15:15 | 23.4031 | 2004-06-03 15:15 | 41.569 | 2004-06-03 15:15 | 659.35
2021-06-03 15:20 | 23.3871 | 41.5958 | 658.13 | 41.6 | 24.2 | 26.075 | 67 | 2004-06-03 15:20 | 23.3871 | 2004-06-03 15:20 | 41.5958 | 2004-06-03 15:20 | 658.13
2021-06-03 15:25 | 23.3769 | 41.6085 | 657.111 | 42 | 24.1 | 26.05 | 67 | 2004-06-03 15:25 | 23.3769 | 2004-06-03 15:25 | 41.6085 | 2004-06-03 15:25 | 657.111
2021-06-03 15:30 | 23.3696 | 41.6141 | 656.193 | 42.9 | 24 | 26.025 | 67 | 2004-06-03 15:30 | 23.3696 | 2004-06-03 15:30 | 41.6141 | 2004-06-03 15:30 | 656.193
2021-06-03 15:35 | 23.364 | 41.6159 | 655.327 | 43.1 | 23.9 | 26 | 67 | 2004-06-03 15:35 | 23.364 | 2004-06-03 15:35 | 41.6159 | 2004-06-03 15:35 | 655.327
2021-06-03 15:40 | 23.3593 | 41.6156 | 654.492 | 42.9 | 23.9 | 25.975 | 67 | 2004-06-03 15:40 | 23.3593 | 2004-06-03 15:40 | 41.6156 | 2004-06-03 15:40 | 654.492
2021-06-03 15:45 | 23.3554 | 41.614 | 653.676 | 43 | 23.9 | 25.95 | 67 | 2004-06-03 15:45 | 23.3554 | 2004-06-03 15:45 | 41.614 | 2004-06-03 15:45 | 653.676
2021-06-03 15:50 | 23.3519 | 41.6115 | 652.873 | 43.4 | 23.8 | 25.925 | 67 | 2004-06-03 15:50 | 23.3519 | 2004-06-03 15:50 | 41.6115 | 2004-06-03 15:50 | 652.873
2021-06-03 15:55 | 23.3489 | 41.6083 | 652.08 | 42.4 | 24.1 | 25.9 | 67 | 2004-06-03 15:55 | 23.3489 | 2004-06-03 15:55 | 41.6083 | 2004-06-03 15:55 | 652.08
2021-06-03 16:00 | 23.5646 | 41.1025 | 651.718 | 42.3 | 24.2 | 25.8583 | 67.4167 | 2004-06-03 16:00 | 23.5646 | 2004-06-03 16:00 | 41.1025 | 2004-06-03 16:00 | 651.718
2021-06-03 16:05 | 23.6683 | 40.883 | 654.175 | 41.7 | 24.2 | 25.8167 | 67.8333 | 2004-06-03 16:05 | 23.6683 | 2004-06-03 16:05 | 40.883 | 2004-06-03 16:05 | 654.175
2021-06-03 16:10 | 23.7237 | 40.7843 | 656.024 | 42 | 24.2 | 25.775 | 68.25 | 2004-06-03 16:10 | 23.7237 | 2004-06-03 16:10 | 40.7843 | 2004-06-03 16:10 | 656.024
2021-06-03 16:15 | 23.7551 | 40.7436 | 657.01 | 42.7 | 24.3 | 25.7333 | 68.6667 | 2004-06-03 16:15 | 23.7551 | 2004-06-03 16:15 | 40.7436 | 2004-06-03 16:15 | 657.01
2021-06-03 16:20 | 23.775 | 40.7296 | 657.576 | 43 | 24.3 | 25.6917 | 69.0833 | 2004-06-03 16:20 | 23.775 | 2004-06-03 16:20 | 40.7296 | 2004-06-03 16:20 | 657.576
2021-06-03 16:25 | 23.7892 | 40.728 | 657.93 | 42.8 | 24.5 | 25.65 | 69.5 | 2004-06-03 16:25 | 23.7892 | 2004-06-03 16:25 | 40.728 | 2004-06-03 16:25 | 657.93
2021-06-03 16:30 | 23.8004 | 40.7321 | 658.173 | 41.6 | 24.5 | 25.6083 | 69.9167 | 2004-06-03 16:30 | 23.8004 | 2004-06-03 16:30 | 40.7321 | 2004-06-03 16:30 | 658.173
2021-06-03 16:35 | 23.8098 | 40.7389 | 658.352 | 41.4 | 24.4 | 25.5667 | 70.3333 | 2004-06-03 16:35 | 23.8098 | 2004-06-03 16:35 | 40.7389 | 2004-06-03 16:35 | 658.352
2021-06-03 16:40 | 23.8182 | 40.7466 | 658.489 | 41.6 | 24.5 | 25.525 | 70.75 | 2004-06-03 16:40 | 23.8182 | 2004-06-03 16:40 | 40.7466 | 2004-06-03 16:40 | 658.489
2021-06-03 16:45 | 23.826 | 40.7546 | 658.599 | 41.5 | 24.5 | 25.4833 | 71.1667 | 2004-06-03 16:45 | 23.826 | 2004-06-03 16:45 | 40.7546 | 2004-06-03 16:45 | 658.599
2021-06-03 16:50 | 23.8333 | 40.7624 | 658.688 | 41.6 | 24.4 | 25.4417 | 71.5833 | 2004-06-03 16:50 | 23.8333 | 2004-06-03 16:50 | 40.7624 | 2004-06-03 16:50 | 658.688
2021-06-03 16:55 | 23.8402 | 40.7701 | 658.76 | 42.9 | 24.4 | 25.4 | 72 | 2004-06-03 16:55 | 23.8402 | 2004-06-03 16:55 | 40.7701 | 2004-06-03 16:55 | 658.76
2021-06-03 17:00 | 23.8463 | 40.7768 | 658.091 | 42.3 | 24.5 | 25.3417 | 72.25 | 2004-06-03 17:00 | 23.8463 | 2004-06-03 17:00 | 40.7768 | 2004-06-03 17:00 | 658.091
2021-06-03 17:05 | 23.8519 | 40.7823 | 657.265 | 42 | 24.6 | 25.2833 | 72.5 | 2004-06-03 17:05 | 23.8519 | 2004-06-03 17:05 | 40.7823 | 2004-06-03 17:05 | 657.265
2021-06-03 17:10 | 23.857 | 40.7865 | 656.415 | 42.1 | 24.6 | 25.225 | 72.75 | 2004-06-03 17:10 | 23.857 | 2004-06-03 17:10 | 40.7865 | 2004-06-03 17:10 | 656.415
2021-06-03 17:15 | 23.8618 | 40.7893 | 655.545 | 43.1 | 24.6 | 25.1667 | 73 | 2004-06-03 17:15 | 23.8618 | 2004-06-03 17:15 | 40.7893 | 2004-06-03 17:15 | 655.545
2021-06-03 17:20 | 23.8664 | 40.7908 | 654.661 | 43.3 | 24.6 | 25.1083 | 73.25 | 2004-06-03 17:20 | 23.8664 | 2004-06-03 17:20 | 40.7908 | 2004-06-03 17:20 | 654.661
2021-06-03 17:25 | 23.8709 | 40.7911 | 653.763 | 43.4 | 24.7 | 25.05 | 73.5 | 2004-06-03 17:25 | 23.8709 | 2004-06-03 17:25 | 40.7911 | 2004-06-03 17:25 | 653.763
2021-06-03 17:30 | 23.9513 | 41.3157 | 652.853 | 43.2 | 24.8 | 24.9917 | 73.75 | 2004-06-03 17:30 | 23.9513 | 2004-06-03 17:30 | 41.3157 | 2004-06-03 17:30 | 652.853
2021-06-03 17:35 | 23.9973 | 41.8372 | 655.588 | 42.9 | 24.9 | 24.9333 | 74 | 2004-06-03 17:35 | 23.9973 | 2004-06-03 17:35 | 41.8372 | 2004-06-03 17:35 | 655.588
2021-06-03 17:40 | 24.0269 | 42.3219 | 658.5 | 43.1 | 24.9 | 24.875 | 74.25 | 2004-06-03 17:40 | 24.0269 | 2004-06-03 17:40 | 42.3219 | 2004-06-03 17:40 | 658.5
2021-06-03 17:45 | 24.0479 | 42.7598 | 660.756 | 43.1 | 25 | 24.8167 | 74.5 | 2004-06-03 17:45 | 24.0479 | 2004-06-03 17:45 | 42.7598 | 2004-06-03 17:45 | 660.756
2021-06-03 17:50 | 24.0643 | 43.1492 | 662.527 | 43 | 25 | 24.7583 | 74.75 | 2004-06-03 17:50 | 24.0643 | 2004-06-03 17:50 | 43.1492 | 2004-06-03 17:50 | 662.527
2021-06-03 17:55 | 24.0781 | 43.4926 | 663.919 | 42.8 | 25 | 24.7 | 75 | 2004-06-03 17:55 | 24.0781 | 2004-06-03 17:55 | 43.4926 | 2004-06-03 17:55 | 663.919
2021-06-03 18:00 | 24.0899 | 43.7936 | 665.159 | 42.8 | 25 | 24.6667 | 75 | 2004-06-03 18:00 | 24.0899 | 2004-06-03 18:00 | 43.7936 | 2004-06-03 18:00 | 665.159
2021-06-03 18:05 | 24.1003 | 44.0566 | 666.101 | 42.7 | 25 | 24.6333 | 75 | 2004-06-03 18:05 | 24.1003 | 2004-06-03 18:05 | 44.0566 | 2004-06-03 18:05 | 666.101
2021-06-03 18:10 | 24.1098 | 44.2855 | 666.814 | 42.5 | 25.1 | 24.6 | 75 | 2004-06-03 18:10 | 24.1098 | 2004-06-03 18:10 | 44.2855 | 2004-06-03 18:10 | 666.814
2021-06-03 18:15 | 24.1185 | 44.4844 | 667.328 | 42.5 | 25.1 | 24.5667 | 75 | 2004-06-03 18:15 | 24.1185 | 2004-06-03 18:15 | 44.4844 | 2004-06-03 18:15 | 667.328
2021-06-03 18:20 | 24.1265 | 44.657 | 667.669 | 42.6 | 25 | 24.5333 | 75 | 2004-06-03 18:20 | 24.1265 | 2004-06-03 18:20 | 44.657 | 2004-06-03 18:20 | 667.669
2021-06-03 18:25 | 24.1339 | 44.8064 | 667.859 | 42.6 | 25 | 24.5 | 75 | 2004-06-03 18:25 | 24.1339 | 2004-06-03 18:25 | 44.8064 | 2004-06-03 18:25 | 667.859
2021-06-03 18:30 | 24.1409 | 44.9354 | 667.917 | 42.5 | 25 | 24.4667 | 75 | 2004-06-03 18:30 | 24.1409 | 2004-06-03 18:30 | 44.9354 | 2004-06-03 18:30 | 667.917
2021-06-03 18:35 | 24.1474 | 45.0467 | 667.858 | 42.6 | 25 | 24.4333 | 75 | 2004-06-03 18:35 | 24.1474 | 2004-06-03 18:35 | 45.0467 | 2004-06-03 18:35 | 667.858
2021-06-03 18:40 | 24.1534 | 45.1424 | 667.697 | 42.6 | 25 | 24.4 | 75 | 2004-06-03 18:40 | 24.1534 | 2004-06-03 18:40 | 45.1424 | 2004-06-03 18:40 | 667.697
2021-06-03 18:45 | 24.1591 | 45.2244 | 667.446 | 42.5 | 25.1 | 24.3667 | 75 | 2004-06-03 18:45 | 24.1591 | 2004-06-03 18:45 | 45.2244 | 2004-06-03 18:45 | 667.446
2021-06-03 18:50 | 24.1643 | 45.2947 | 667.117 | 42.4 | 25.1 | 24.3333 | 75 | 2004-06-03 18:50 | 24.1643 | 2004-06-03 18:50 | 45.2947 | 2004-06-03 18:50 | 667.117
2021-06-03 18:55 | 24.1691 | 45.3547 | 666.716 | 42.4 | 25.1 | 24.3 | 75 | 2004-06-03 18:55 | 24.1691 | 2004-06-03 18:55 | 45.3547 | 2004-06-03 18:55 | 666.716
2021-06-03 19:00 | 24.1739 | 45.4055 | 666.399 | 42.5 | 25 | 24.2667 | 75.0833 | 2004-06-03 19:00 | 24.1739 | 2004-06-03 19:00 | 45.4055 | 2004-06-03 19:00 | 666.399
2021-06-03 19:05 | 24.1785 | 45.4487 | 666.069 | 42.5 | 25.1 | 24.2333 | 75.1667 | 2004-06-03 19:05 | 24.1785 | 2004-06-03 19:05 | 45.4487 | 2004-06-03 19:05 | 666.069
2021-06-03 19:10 | 24.1829 | 45.4853 | 665.694 | 42.3 | 25.1 | 24.2 | 75.25 | 2004-06-03 19:10 | 24.1829 | 2004-06-03 19:10 | 45.4853 | 2004-06-03 19:10 | 665.694
2021-06-03 19:15 | 24.187 | 45.5161 | 665.281 | 40.7 | 25.1 | 24.1667 | 75.3333 | 2004-06-03 19:15 | 24.187 | 2004-06-03 19:15 | 45.5161 | 2004-06-03 19:15 | 665.281
2021-06-03 19:20 | 24.191 | 45.542 | 664.833 | 40.3 | 25 | 24.1333 | 75.4167 | 2004-06-03 19:20 | 24.191 | 2004-06-03 19:20 | 45.542 | 2004-06-03 19:20 | 664.833
2021-06-03 19:25 | 24.1947 | 45.5636 | 664.353 | 40.3 | 25 | 24.1 | 75.5 | 2004-06-03 19:25 | 24.1947 | 2004-06-03 19:25 | 45.5636 | 2004-06-03 19:25 | 664.353
2021-06-03 19:30 | 24.1982 | 45.5815 | 663.847 | 41.6 | 25 | 24.0667 | 75.5833 | 2004-06-03 19:30 | 24.1982 | 2004-06-03 19:30 | 45.5815 | 2004-06-03 19:30 | 663.847
2021-06-03 19:35 | 24.2015 | 45.5961 | 663.316 | 42 | 25.1 | 24.0333 | 75.6667 | 2004-06-03 19:35 | 24.2015 | 2004-06-03 19:35 | 45.5961 | 2004-06-03 19:35 | 663.316
2021-06-03 19:40 | 24.2046 | 45.6079 | 662.763 | 42.2 | 25.3 | 24 | 75.75 | 2004-06-03 19:40 | 24.2046 | 2004-06-03 19:40 | 45.6079 | 2004-06-03 19:40 | 662.763
2021-06-03 19:45 | 24.2076 | 45.6173 | 662.568 | 43 | 25.6 | 23.9667 | 75.8333 | 2004-06-03 19:45 | 24.2076 | 2004-06-03 19:45 | 45.6173 | 2004-06-03 19:45 | 662.568
2021-06-03 19:50 | 24.2104 | 45.6246 | 662.355 | 42.1 | 25.5 | 23.9333 | 75.9167 | 2004-06-03 19:50 | 24.2104 | 2004-06-03 19:50 | 45.6246 | 2004-06-03 19:50 | 662.355
2021-06-03 19:55 | 24.213 | 45.6301 | 662.127 | 43.1 | 25.3 | 23.9 | 76 | 2004-06-03 19:55 | 24.213 | 2004-06-03 19:55 | 45.6301 | 2004-06-03 19:55 | 662.127
2021-06-03 20:00 | 24.2655 | 46.3465 | 662.061 | 43.1 | 25.1 | 23.8583 | 76.25 | 2004-06-03 20:00 | 24.2655 | 2004-06-03 20:00 | 46.3465 | 2004-06-03 20:00 | 662.061
2021-06-03 20:05 | 24.2964 | 47.0051 | 663.998 | 42.8 | 25 | 23.8167 | 76.5 | 2004-06-03 20:05 | 24.2964 | 2004-06-03 20:05 | 47.0051 | 2004-06-03 20:05 | 663.998
2021-06-03 20:10 | 24.3166 | 47.5913 | 665.984 | 43 | 24.9 | 23.775 | 76.75 | 2004-06-03 20:10 | 24.3166 | 2004-06-03 20:10 | 47.5913 | 2004-06-03 20:10 | 665.984
2021-06-03 20:15 | 24.3312 | 48.1057 | 667.589 | 43.4 | 24.8 | 23.7333 | 77 | 2004-06-03 20:15 | 24.3312 | 2004-06-03 20:15 | 48.1057 | 2004-06-03 20:15 | 667.589
2021-06-03 20:20 | 24.3425 | 48.5537 | 668.926 | 43 | 24.9 | 23.6917 | 77.25 | 2004-06-03 20:20 | 24.3425 | 2004-06-03 20:20 | 48.5537 | 2004-06-03 20:20 | 668.926
2021-06-03 20:25 | 24.3518 | 48.9421 | 670.059 | 43.4 | 24.8 | 23.65 | 77.5 | 2004-06-03 20:25 | 24.3518 | 2004-06-03 20:25 | 48.9421 | 2004-06-03 20:25 | 670.059
2021-06-03 20:30 | 24.1058 | 49.6021 | 670.376 | 43.7 | 24.8 | 23.6083 | 77.75 | 2004-06-03 20:30 | 24.1058 | 2004-06-03 20:30 | 49.6021 | 2004-06-03 20:30 | 670.376
2021-06-03 20:35 | 23.8924 | 50.1174 | 667.883 | 44.8 | 24.6 | 23.5667 | 78 | 2004-06-03 20:35 | 23.8924 | 2004-06-03 20:35 | 50.1174 | 2004-06-03 20:35 | 667.883
2021-06-03 20:40 | 23.8194 | 50.2369 | 666.298 | 44.4 | 24.6 | 23.525 | 78.25 | 2004-06-03 20:40 | 23.8194 | 2004-06-03 20:40 | 50.2369 | 2004-06-03 20:40 | 666.298
2021-06-03 20:45 | 23.7811 | 50.2587 | 665.482 | 44.3 | 24.5 | 23.4833 | 78.5 | 2004-06-03 20:45 | 23.7811 | 2004-06-03 20:45 | 50.2587 | 2004-06-03 20:45 | 665.482
2021-06-03 20:50 | 23.7586 | 50.2412 | 665.164 | 44.6 | 24.4 | 23.4417 | 78.75 | 2004-06-03 20:50 | 23.7586 | 2004-06-03 20:50 | 50.2412 | 2004-06-03 20:50 | 665.164
2021-06-03 20:55 | 23.7437 | 50.2098 | 665.052 | 44.5 | 24.3 | 23.4 | 79 | 2004-06-03 20:55 | 23.7437 | 2004-06-03 20:55 | 50.2098 | 2004-06-03 20:55 | 665.052
2021-06-03 21:00 | 23.7324 | 50.1748 | 664.709 | 45.7 | 24 | 23.3667 | 79 | 2004-06-03 21:00 | 23.7324 | 2004-06-03 21:00 | 50.1748 | 2004-06-03 21:00 | 664.709
2021-06-03 21:05 | 23.7231 | 50.1405 | 664.3 | 48.7 | 23.8 | 23.3333 | 79 | 2004-06-03 21:05 | 23.7231 | 2004-06-03 21:05 | 50.1405 | 2004-06-03 21:05 | 664.3
2021-06-03 21:10 | 23.7149 | 50.1086 | 663.88 | 54.7 | 23.7 | 23.3 | 79 | 2004-06-03 21:10 | 23.7149 | 2004-06-03 21:10 | 50.1086 | 2004-06-03 21:10 | 663.88
2021-06-03 21:15 | 23.7075 | 50.0798 | 663.441 | 58 | 23.6 | 23.2667 | 79 | 2004-06-03 21:15 | 23.7075 | 2004-06-03 21:15 | 50.0798 | 2004-06-03 21:15 | 663.441
2021-06-03 21:20 | 23.7007 | 50.054 | 662.981 | 71.5 | 23.5 | 23.2333 | 79 | 2004-06-03 21:20 | 23.7007 | 2004-06-03 21:20 | 50.054 | 2004-06-03 21:20 | 662.981
2021-06-03 21:25 | 23.6944 | 50.0311 | 662.501 | 64.6 | 23.3 | 23.2 | 79 | 2004-06-03 21:25 | 23.6944 | 2004-06-03 21:25 | 50.0311 | 2004-06-03 21:25 | 662.501
2021-06-03 21:30 | 23.5805 | 50.337 | 662.003 | 58.7 | 23.1 | 23.1667 | 79 | 2004-06-03 21:30 | 23.5805 | 2004-06-03 21:30 | 50.337 | 2004-06-03 21:30 | 662.003
2021-06-03 21:35 | 23.5255 | 50.4602 | 660.32 | 57.1 | 23.1 | 23.1333 | 79 | 2004-06-03 21:35 | 23.5255 | 2004-06-03 21:35 | 50.4602 | 2004-06-03 21:35 | 660.32
2021-06-03 21:40 | 23.4949 | 50.5092 | 658.94 | 55.4 | 23 | 23.1 | 79 | 2004-06-03 21:40 | 23.4949 | 2004-06-03 21:40 | 50.5092 | 2004-06-03 21:40 | 658.94
2021-06-03 21:45 | 23.476 | 50.5249 | 657.947 | 56 | 22.8 | 23.0667 | 79 | 2004-06-03 21:45 | 23.476 | 2004-06-03 21:45 | 50.5249 | 2004-06-03 21:45 | 657.947
2021-06-03 21:50 | 23.4623 | 50.527 | 657.127 | 52.1 | 22.7 | 23.0333 | 79 | 2004-06-03 21:50 | 23.4623 | 2004-06-03 21:50 | 50.527 | 2004-06-03 21:50 | 657.127
2021-06-03 21:55 | 23.4514 | 50.5238 | 656.385 | 50.5 | 22.5 | 23 | 79 | 2004-06-03 21:55 | 23.4514 | 2004-06-03 21:55 | 50.5238 | 2004-06-03 21:55 | 656.385
2021-06-03 22:00 | 23.4994 | 50.6916 | 655.709 | 47.5 | 22.4 | 22.9583 | 79.0833 | 2004-06-03 22:00 | 23.4994 | 2004-06-03 22:00 | 50.6916 | 2004-06-03 22:00 | 655.709
2021-06-03 22:05 | 23.5192 | 50.9087 | 657.05 | 47.1 | 22.3 | 22.9167 | 79.1667 | 2004-06-03 22:05 | 23.5192 | 2004-06-03 22:05 | 50.9087 | 2004-06-03 22:05 | 657.05
2021-06-03 22:10 | 23.5271 | 51.1278 | 658.487 | 46.4 | 22.1 | 22.875 | 79.25 | 2004-06-03 22:10 | 23.5271 | 2004-06-03 22:10 | 51.1278 | 2004-06-03 22:10 | 658.487
2021-06-03 22:15 | 23.5295 | 51.333 | 659.555 | 46.6 | 22 | 22.8333 | 79.3333 | 2004-06-03 22:15 | 23.5295 | 2004-06-03 22:15 | 51.333 | 2004-06-03 22:15 | 659.555
2021-06-03 22:20 | 23.5293 | 51.5184 | 660.358 | 46.3 | 22 | 22.7917 | 79.4167 | 2004-06-03 22:20 | 23.5293 | 2004-06-03 22:20 | 51.5184 | 2004-06-03 22:20 | 660.358
2021-06-03 22:25 | 23.528 | 51.6832 | 660.962 | 46.3 | 21.9 | 22.75 | 79.5 | 2004-06-03 22:25 | 23.528 | 2004-06-03 22:25 | 51.6832 | 2004-06-03 22:25 | 660.962
2021-06-03 22:30 | 23.5261 | 51.8285 | 661.407 | 46 | 21.9 | 22.7083 | 79.5833 | 2004-06-03 22:30 | 23.5261 | 2004-06-03 22:30 | 51.8285 | 2004-06-03 22:30 | 661.407
2021-06-03 22:35 | 23.5238 | 51.9563 | 661.719 | 46.3 | 21.8 | 22.6667 | 79.6667 | 2004-06-03 22:35 | 23.5238 | 2004-06-03 22:35 | 51.9563 | 2004-06-03 22:35 | 661.719
2021-06-03 22:40 | 23.5214 | 52.0683 | 661.917 | 48.9 | 21.9 | 22.625 | 79.75 | 2004-06-03 22:40 | 23.5214 | 2004-06-03 22:40 | 52.0683 | 2004-06-03 22:40 | 661.917
2021-06-03 22:45 | 23.5188 | 52.1665 | 662.017 | 49.6 | 22.1 | 22.5833 | 79.8333 | 2004-06-03 22:45 | 23.5188 | 2004-06-03 22:45 | 52.1665 | 2004-06-03 22:45 | 662.017
2021-06-03 22:50 | 23.5161 | 52.2524 | 662.033 | 48 | 22.3 | 22.5417 | 79.9167 | 2004-06-03 22:50 | 23.5161 | 2004-06-03 22:50 | 52.2524 | 2004-06-03 22:50 | 662.033
2021-06-03 22:55 | 23.5133 | 52.3277 | 661.974 | 48 | 22.4 | 22.5 | 80 | 2004-06-03 22:55 | 23.5133 | 2004-06-03 22:55 | 52.3277 | 2004-06-03 22:55 | 661.974
2021-06-03 23:00 | 23.4393 | 50.8715 | 662.316 | 47.2 | 22.5 | 22.45 | 80.4167 | 2004-06-03 23:00 | 23.4393 | 2004-06-03 23:00 | 50.8715 | 2004-06-03 23:00 | 662.316
2021-06-03 23:05 | 23.3911 | 49.5373 | 654.694 | 46.7 | 22.5 | 22.4 | 80.8333 | 2004-06-03 23:05 | 23.3911 | 2004-06-03 23:05 | 49.5373 | 2004-06-03 23:05 | 654.694
2021-06-03 23:10 | 23.3567 | 48.3395 | 646.516 | 45.3 | 22.6 | 22.35 | 81.25 | 2004-06-03 23:10 | 23.3567 | 2004-06-03 23:10 | 48.3395 | 2004-06-03 23:10 | 646.516
2021-06-03 23:15 | 23.3293 | 47.2768 | 639.685 | 46.3 | 22.6 | 22.3 | 81.6667 | 2004-06-03 23:15 | 23.3293 | 2004-06-03 23:15 | 47.2768 | 2004-06-03 23:15 | 639.685
2021-06-03 23:20 | 23.306 | 46.3396 | 633.773 | 45.3 | 22.6 | 22.25 | 82.0833 | 2004-06-03 23:20 | 23.306 | 2004-06-03 23:20 | 46.3396 | 2004-06-03 23:20 | 633.773
2021-06-03 23:25 | 23.2855 | 45.5159 | 628.594 | 45.5 | 22.6 | 22.2 | 82.5 | 2004-06-03 23:25 | 23.2855 | 2004-06-03 23:25 | 45.5159 | 2004-06-03 23:25 | 628.594
2021-06-03 23:30 | 23.2669 | 44.7936 | 624.046 | 45 | 22.6 | 22.15 | 82.9167 | 2004-06-03 23:30 | 23.2669 | 2004-06-03 23:30 | 44.7936 | 2004-06-03 23:30 | 624.046
2021-06-03 23:35 | 23.2499 | 44.1607 | 620.044 | 45.8 | 22.7 | 22.1 | 83.3333 | 2004-06-03 23:35 | 23.2499 | 2004-06-03 23:35 | 44.1607 | 2004-06-03 23:35 | 620.044
2021-06-03 23:40 | 23.2343 | 43.607 | 616.52 | 44.4 | 22.7 | 22.05 | 83.75 | 2004-06-03 23:40 | 23.2343 | 2004-06-03 23:40 | 43.607 | 2004-06-03 23:40 | 616.52
2021-06-03 23:45 | 23.2197 | 43.123 | 613.415 | 44.8 | 22.7 | 22 | 84.1667 | 2004-06-03 23:45 | 23.2197 | 2004-06-03 23:45 | 43.123 | 2004-06-03 23:45 | 613.415
2021-06-03 23:50 | 23.2062 | 42.7002 | 610.676 | 44.3 | 22.7 | 21.95 | 84.5833 | 2004-06-03 23:50 | 23.2062 | 2004-06-03 23:50 | 42.7002 | 2004-06-03 23:50 | 610.676
2021-06-03 23:55 | 23.1935 | 42.3312 | 608.258 | 44.9 | 22.7 | 21.9 | 85 | 2004-06-03 23:55 | 23.1935 | 2004-06-03 23:55 | 42.3312 | 2004-06-03 23:55 | 608.258
|  |  |  | 42.8454 | 24.2639
|  |  |  | 42.8454 | 24.2639
|  |  |  | 100% | 100%
Formulas:
Date/Time = [Date/Time, row above]+1/(24*12)

## ANN mentah
| INPUT |  | OUTPUT
Date/Time | Zone Mean Air Temperature FILLING B [C] | Zone Air Relative Humidity FILLING B [%] | Fan Coil Total Cooling Rate FILLING B FAN COIL [W]
2021-06-03 | 22.8826 | 41.842 | 1234.98
2021-06-03 00:05 | 22.8723 | 41.5893 | 1224.14
2021-06-03 00:10 | 22.8627 | 41.372 | 1214.6
2021-06-03 00:15 | 22.8537 | 41.1857 | 1206.21
2021-06-03 00:20 | 22.8453 | 41.0262 | 1198.81
2021-06-03 00:25 | 22.8374 | 40.8902 | 1192.27
2021-06-03 00:30 | 22.8299 | 40.7746 | 1186.49
2021-06-03 00:35 | 22.8228 | 40.6767 | 1181.37
2021-06-03 00:40 | 22.8161 | 40.5941 | 1176.82
2021-06-03 00:45 | 22.8098 | 40.525 | 1172.77
2021-06-03 00:50 | 22.8037 | 40.4674 | 1169.16
2021-06-03 00:55 | 22.798 | 40.4199 | 1165.93
2021-06-03 01:00 | 22.7918 | 40.382 | 1164.2
2021-06-03 01:05 | 22.7854 | 40.35 | 1162.63
2021-06-03 01:10 | 22.7792 | 40.323 | 1161.22
2021-06-03 01:15 | 22.7731 | 40.2999 | 1159.95
2021-06-03 01:20 | 22.7672 | 40.2802 | 1158.83
2021-06-03 01:25 | 22.7614 | 40.2635 | 1157.82
2021-06-03 01:30 | 22.7557 | 40.2495 | 1156.92
2021-06-03 01:35 | 22.7502 | 40.2377 | 1156.12
2021-06-03 01:40 | 22.7447 | 40.2278 | 1155.39
2021-06-03 01:45 | 22.7394 | 40.2195 | 1154.74
2021-06-03 01:50 | 22.7342 | 40.2126 | 1154.15
2021-06-03 01:55 | 22.7291 | 40.2069 | 1153.61
2021-06-03 02:00 | 22.7244 | 40.2028 | 1152.53
2021-06-03 02:05 | 22.7201 | 40.2004 | 1151.56
2021-06-03 02:10 | 22.7159 | 40.1995 | 1150.68
2021-06-03 02:15 | 22.7119 | 40.2001 | 1149.87
2021-06-03 02:20 | 22.708 | 40.202 | 1149.12
2021-06-03 02:25 | 22.7042 | 40.2049 | 1148.43
2021-06-03 02:30 | 22.7005 | 40.2088 | 1147.79
2021-06-03 02:35 | 22.6969 | 40.2135 | 1147.19
2021-06-03 02:40 | 22.6934 | 40.2189 | 1146.63
2021-06-03 02:45 | 22.6899 | 40.2248 | 1146.1
2021-06-03 02:50 | 22.6866 | 40.2313 | 1145.6
2021-06-03 02:55 | 22.6833 | 40.2381 | 1145.13
2021-06-03 03:00 | 22.6806 | 40.246 | 1143.83
2021-06-03 03:05 | 22.6783 | 40.2553 | 1142.65
2021-06-03 03:10 | 22.6762 | 40.266 | 1141.57
2021-06-03 03:15 | 22.6742 | 40.278 | 1140.56
2021-06-03 03:20 | 22.6724 | 40.2912 | 1139.61
2021-06-03 03:25 | 22.6706 | 40.3053 | 1138.72
2021-06-03 03:30 | 22.6689 | 40.3204 | 1137.87
2021-06-03 03:35 | 22.6673 | 40.3362 | 1137.06
2021-06-03 03:40 | 22.6658 | 40.3526 | 1136.29
2021-06-03 03:45 | 22.6643 | 40.3696 | 1135.55
2021-06-03 03:50 | 22.663 | 40.387 | 1134.83
2021-06-03 03:55 | 22.6616 | 40.4047 | 1134.15
2021-06-03 04:00 | 22.6592 | 40.4212 | 1135.35
2021-06-03 04:05 | 22.6562 | 40.4355 | 1136.36
2021-06-03 04:10 | 22.653 | 40.4473 | 1137.22
2021-06-03 04:15 | 22.6496 | 40.4567 | 1137.97
2021-06-03 04:20 | 22.6462 | 40.4641 | 1138.64
2021-06-03 04:25 | 22.6428 | 40.4694 | 1139.23
2021-06-03 04:30 | 22.6393 | 40.4731 | 1139.76
2021-06-03 04:35 | 22.6358 | 40.4753 | 1140.24
2021-06-03 04:40 | 22.6323 | 40.4762 | 1140.68
2021-06-03 04:45 | 22.6288 | 40.476 | 1141.07
2021-06-03 04:50 | 22.6252 | 40.4748 | 1141.43
2021-06-03 04:55 | 22.6217 | 40.4727 | 1141.76
2021-06-03 05:00 | 22.6192 | 40.471 | 1140.56
2021-06-03 05:05 | 22.6171 | 40.4707 | 1139.52
2021-06-03 05:10 | 22.6153 | 40.4719 | 1138.59
2021-06-03 05:15 | 22.6136 | 40.4746 | 1137.74
2021-06-03 05:20 | 22.612 | 40.4787 | 1136.95
2021-06-03 05:25 | 22.6105 | 40.484 | 1136.22
2021-06-03 05:30 | 22.6091 | 40.4904 | 1135.54
2021-06-03 05:35 | 22.6078 | 40.4978 | 1134.89
2021-06-03 05:40 | 22.6065 | 40.5059 | 1134.28
2021-06-03 05:45 | 22.6052 | 40.5148 | 1133.71
2021-06-03 05:50 | 22.604 | 40.5243 | 1133.15
2021-06-03 05:55 | 22.6028 | 40.5342 | 1132.63
2021-06-03 06:00 | 22.6016 | 40.5445 | 1132.2
2021-06-03 06:05 | 22.6005 | 40.5551 | 1131.78
2021-06-03 06:10 | 22.5994 | 40.5658 | 1131.37
2021-06-03 06:15 | 22.5983 | 40.5767 | 1130.97
2021-06-03 06:20 | 22.5972 | 40.5877 | 1130.58
2021-06-03 06:25 | 22.5962 | 40.5989 | 1130.2
2021-06-03 06:30 | 22.5952 | 40.6101 | 1129.82
2021-06-03 06:35 | 22.5942 | 40.6214 | 1129.45
2021-06-03 06:40 | 22.5933 | 40.6327 | 1129.08
2021-06-03 06:45 | 22.5924 | 40.6441 | 1128.72
2021-06-03 06:50 | 22.5915 | 40.6555 | 1128.36
2021-06-03 06:55 | 22.5907 | 40.6669 | 1128.01
2021-06-03 07:00 | 22.5894 | 40.6778 | 1128.3
2021-06-03 07:05 | 22.588 | 40.6878 | 1128.53
2021-06-03 07:10 | 22.5865 | 40.6969 | 1128.71
2021-06-03 07:15 | 22.585 | 40.7051 | 1128.86
2021-06-03 07:20 | 22.5834 | 40.7124 | 1128.98
2021-06-03 07:25 | 22.5819 | 40.719 | 1129.08
2021-06-03 07:30 | 22.5803 | 40.7249 | 1129.16
2021-06-03 07:35 | 22.5787 | 40.7303 | 1129.23
2021-06-03 07:40 | 22.5771 | 40.735 | 1129.28
2021-06-03 07:45 | 22.5755 | 40.7393 | 1129.32
2021-06-03 07:50 | 22.5739 | 40.7432 | 1129.36
2021-06-03 07:55 | 22.5722 | 40.7467 | 1129.38
2021-06-03 08:00 | 22.5714 | 40.7508 | 1128.16
2021-06-03 08:05 | 22.571 | 40.7562 | 1127.06
2021-06-03 08:10 | 22.5708 | 40.7631 | 1126.06
2021-06-03 08:15 | 22.5707 | 40.7715 | 1125.13
2021-06-03 08:20 | 22.5708 | 40.7812 | 1124.26
2021-06-03 08:25 | 22.5709 | 40.792 | 1123.43
2021-06-03 08:30 | 22.571 | 40.8039 | 1122.64
2021-06-03 08:35 | 22.5713 | 40.8167 | 1121.89
2021-06-03 08:40 | 22.5715 | 40.8302 | 1121.17
2021-06-03 08:45 | 22.5719 | 40.8444 | 1120.48
2021-06-03 08:50 | 22.5723 | 40.8592 | 1119.8
2021-06-03 08:55 | 22.5727 | 40.8746 | 1119.15
2021-06-03 09:00 | 22.5718 | 40.8885 | 1120.8
2021-06-03 09:05 | 22.5701 | 40.8997 | 1122.23
2021-06-03 09:10 | 22.5681 | 40.9079 | 1123.5
2021-06-03 09:15 | 22.566 | 40.9132 | 1124.65
2021-06-03 09:20 | 22.5636 | 40.9158 | 1125.72
2021-06-03 09:25 | 22.5612 | 40.9159 | 1126.71
2021-06-03 09:30 | 22.5587 | 40.9138 | 1127.64
2021-06-03 09:35 | 22.5563 | 40.9095 | 1128.52
2021-06-03 09:40 | 22.5537 | 40.9037 | 1129.37
2021-06-03 09:45 | 22.5511 | 40.896 | 1130.17
2021-06-03 09:50 | 22.5485 | 40.8868 | 1130.95
2021-06-03 09:55 | 22.5457 | 40.8767 | 1131.71
2021-06-03 10:00 | 22.7566 | 40.3421 | 1130.96
2021-06-03 10:05 | 22.8558 | 40.0894 | 1146.78
2021-06-03 10:10 | 22.9077 | 39.955 | 1154.08
2021-06-03 10:15 | 22.9365 | 39.8784 | 1157.79
2021-06-03 10:20 | 22.9543 | 39.8296 | 1159.78
2021-06-03 10:25 | 22.9666 | 39.795 | 1160.95
2021-06-03 10:30 | 22.9761 | 39.7681 | 1161.74
2021-06-03 10:35 | 22.9838 | 39.746 | 1162.32
2021-06-03 10:40 | 22.9906 | 39.7268 | 1162.8
2021-06-03 10:45 | 22.9967 | 39.7096 | 1163.22
2021-06-03 10:50 | 23.0021 | 39.6942 | 1163.61
2021-06-03 10:55 | 23.1854 | 40.0122 | 1163.97
2021-06-03 11:00 | 23.2542 | 39.9165 | 1197.09
2021-06-03 11:05 | 23.2972 | 39.8838 | 1201.29
2021-06-03 11:10 | 23.3272 | 39.8824 | 1203.51
2021-06-03 11:15 | 23.3503 | 39.8967 | 1204.7
2021-06-03 11:20 | 23.3699 | 39.9189 | 1205.33
2021-06-03 11:25 | 23.3874 | 39.9451 | 1205.63
2021-06-03 11:30 | 23.4037 | 39.9734 | 1205.75
2021-06-03 11:35 | 23.4191 | 40.0031 | 1205.73
2021-06-03 11:40 | 23.434 | 40.0336 | 1205.61
2021-06-03 11:45 | 23.4484 | 40.0647 | 1205.41
2021-06-03 11:50 | 23.4624 | 40.0963 | 1205.15
2021-06-03 11:55 | 23.4761 | 40.1283 | 1204.82
2021-06-03 12:00 | 23.4299 | 40.2337 | 1206.4
2021-06-03 12:05 | 23.4114 | 40.2751 | 1201.22
2021-06-03 12:10 | 23.4055 | 40.2889 | 1198.25
2021-06-03 12:15 | 23.4059 | 40.2907 | 1196.34
2021-06-03 12:20 | 23.4093 | 40.2882 | 1195.01
2021-06-03 12:25 | 23.4141 | 40.2848 | 1193.99
2021-06-03 12:30 | 23.4206 | 40.3108 | 1193.15
2021-06-03 12:35 | 23.4272 | 40.335 | 1193.44
2021-06-03 12:40 | 23.4339 | 40.3576 | 1193.68
2021-06-03 12:45 | 23.4405 | 40.3788 | 1193.87
2021-06-03 12:50 | 23.4472 | 40.3989 | 1194.03
2021-06-03 12:55 | 23.454 | 40.418 | 1194.15
2021-06-03 13:00 | 23.4577 | 40.4327 | 1198.87
2021-06-03 13:05 | 23.4599 | 40.4402 | 1203.01
2021-06-03 13:10 | 23.4612 | 40.4403 | 1206.73
2021-06-03 13:15 | 23.4621 | 40.4335 | 1210.12
2021-06-03 13:20 | 23.4626 | 40.4201 | 1213.24
2021-06-03 13:25 | 23.4628 | 40.4011 | 1216.14
2021-06-03 13:30 | 23.4617 | 40.3515 | 1218.84
2021-06-03 13:35 | 23.4608 | 40.3007 | 1220.46
2021-06-03 13:40 | 23.46 | 40.249 | 1222.1
2021-06-03 13:45 | 23.4592 | 40.1968 | 1223.74
2021-06-03 13:50 | 23.4583 | 40.1442 | 1225.37
2021-06-03 13:55 | 23.4573 | 40.0912 | 1227.01
2021-06-03 14:00 | 23.464 | 40.2072 | 1227.31
2021-06-03 14:05 | 23.4684 | 40.3074 | 1233.8
2021-06-03 14:10 | 23.4716 | 40.3916 | 1239.46
2021-06-03 14:15 | 23.4742 | 40.461 | 1244.47
2021-06-03 14:20 | 23.4763 | 40.5169 | 1248.94
2021-06-03 14:25 | 23.4782 | 40.5611 | 1252.96
2021-06-03 14:30 | 23.4799 | 40.5949 | 1256.58
2021-06-03 14:35 | 23.4814 | 40.6196 | 1259.87
2021-06-03 14:40 | 23.4828 | 40.6364 | 1262.86
2021-06-03 14:45 | 23.4841 | 40.6464 | 1265.6
2021-06-03 14:50 | 23.4852 | 40.6504 | 1268.11
2021-06-03 14:55 | 23.4862 | 40.6492 | 1270.43
2021-06-03 15:00 | 23.2715 | 41.18 | 1270.93
2021-06-03 15:05 | 23.1733 | 41.4179 | 1254.69
2021-06-03 15:10 | 23.1245 | 41.5303 | 1247.26
2021-06-03 15:15 | 23.0991 | 41.5832 | 1243.57
2021-06-03 15:20 | 23.0843 | 41.6089 | 1241.66
2021-06-03 15:25 | 23.0749 | 41.6216 | 1240.57
2021-06-03 15:30 | 23.0681 | 41.6279 | 1239.88
2021-06-03 15:35 | 23.0628 | 41.6307 | 1239.42
2021-06-03 15:40 | 23.0585 | 41.6315 | 1239.08
2021-06-03 15:45 | 23.0547 | 41.6312 | 1238.83
2021-06-03 15:50 | 23.0515 | 41.6298 | 1238.63
2021-06-03 15:55 | 23.0486 | 41.6278 | 1238.47
2021-06-03 16:00 | 23.2623 | 41.1271 | 1237.19
2021-06-03 16:05 | 23.3624 | 40.9167 | 1253.93
2021-06-03 16:10 | 23.4148 | 40.8251 | 1262.01
2021-06-03 16:15 | 23.4441 | 40.7889 | 1266.4
2021-06-03 16:20 | 23.4627 | 40.7773 | 1268.97
2021-06-03 16:25 | 23.476 | 40.7767 | 1270.66
2021-06-03 16:30 | 23.4866 | 40.7808 | 1271.88
2021-06-03 16:35 | 23.4956 | 40.7869 | 1272.84
2021-06-03 16:40 | 23.5036 | 40.7937 | 1273.63
2021-06-03 16:45 | 23.5111 | 40.8003 | 1274.31
2021-06-03 16:50 | 23.5182 | 40.8068 | 1274.91
2021-06-03 16:55 | 23.5249 | 40.8128 | 1275.44
2021-06-03 17:00 | 23.5309 | 40.818 | 1276.72
2021-06-03 17:05 | 23.5364 | 40.8218 | 1277.86
2021-06-03 17:10 | 23.5414 | 40.8245 | 1278.9
2021-06-03 17:15 | 23.5461 | 40.8258 | 1279.83
2021-06-03 17:20 | 23.5507 | 40.8259 | 1280.69
2021-06-03 17:25 | 23.5551 | 40.8249 | 1281.48
2021-06-03 17:30 | 23.6367 | 41.3475 | 1282.22
2021-06-03 17:35 | 23.6821 | 41.8665 | 1310.42
2021-06-03 17:40 | 23.7108 | 42.3456 | 1333.15
2021-06-03 17:45 | 23.7309 | 42.7749 | 1352.19
2021-06-03 17:50 | 23.7466 | 43.1533 | 1368.46
2021-06-03 17:55 | 23.7598 | 43.4839 | 1382.53
2021-06-03 18:00 | 23.7711 | 43.7711 | 1395.17
2021-06-03 18:05 | 23.7812 | 44.0197 | 1406.22
2021-06-03 18:10 | 23.7903 | 44.2342 | 1415.9
2021-06-03 18:15 | 23.7987 | 44.4188 | 1424.41
2021-06-03 18:20 | 23.8065 | 44.5774 | 1431.89
2021-06-03 18:25 | 23.8137 | 44.7134 | 1438.49
2021-06-03 18:30 | 23.8205 | 44.8296 | 1444.31
2021-06-03 18:35 | 23.8267 | 44.9289 | 1449.46
2021-06-03 18:40 | 23.8326 | 45.0133 | 1454.01
2021-06-03 18:45 | 23.8382 | 45.0847 | 1458.05
2021-06-03 18:50 | 23.8432 | 45.1454 | 1461.64
2021-06-03 18:55 | 23.848 | 45.1963 | 1464.82
2021-06-03 19:00 | 23.8527 | 45.2389 | 1467.4
2021-06-03 19:05 | 23.8572 | 45.2745 | 1469.71
2021-06-03 19:10 | 23.8614 | 45.3042 | 1471.78
2021-06-03 19:15 | 23.8655 | 45.3287 | 1473.64
2021-06-03 19:20 | 23.8694 | 45.3489 | 1475.3
2021-06-03 19:25 | 23.873 | 45.3654 | 1476.8
2021-06-03 19:30 | 23.8765 | 45.3785 | 1478.14
2021-06-03 19:35 | 23.8798 | 45.389 | 1479.36
2021-06-03 19:40 | 23.8828 | 45.397 | 1480.47
2021-06-03 19:45 | 23.8858 | 45.403 | 1481.47
2021-06-03 19:50 | 23.8885 | 45.4073 | 1482.38
2021-06-03 19:55 | 23.8911 | 45.4101 | 1483.21
2021-06-03 20:00 | 23.9491 | 46.1363 | 1483.6
2021-06-03 20:05 | 23.9816 | 46.8051 | 1515.26
2021-06-03 20:10 | 24.0023 | 47.3978 | 1541.15
2021-06-03 20:15 | 24.0168 | 47.9143 | 1562.83
2021-06-03 20:20 | 24.028 | 48.3604 | 1581.18
2021-06-03 20:25 | 24.0372 | 48.7442 | 1596.81
2021-06-03 20:30 | 23.79 | 49.3798 | 1602.73
2021-06-03 20:35 | 23.5806 | 49.8423 | 1583.14
2021-06-03 20:40 | 23.5108 | 49.9258 | 1568.43
2021-06-03 20:45 | 23.4746 | 49.9195 | 1559.26
2021-06-03 20:50 | 23.4533 | 49.8804 | 1552.92
2021-06-03 20:55 | 23.4391 | 49.8321 | 1548.09
2021-06-03 21:00 | 23.4282 | 49.7838 | 1544.59
2021-06-03 21:05 | 23.4192 | 49.7388 | 1541.66
2021-06-03 21:10 | 23.4112 | 49.6984 | 1539.15
2021-06-03 21:15 | 23.404 | 49.6628 | 1536.97
2021-06-03 21:20 | 23.3973 | 49.6316 | 1535.06
2021-06-03 21:25 | 23.3911 | 49.6044 | 1533.38
2021-06-03 21:30 | 23.2784 | 49.9015 | 1531.9
2021-06-03 21:35 | 23.2252 | 50.016 | 1522.73
2021-06-03 21:40 | 23.196 | 50.0591 | 1517.79
2021-06-03 21:45 | 23.1779 | 50.0712 | 1514.66
2021-06-03 21:50 | 23.1649 | 50.0712 | 1512.42
2021-06-03 21:55 | 23.1544 | 50.067 | 1510.66
2021-06-03 22:00 | 23.2034 | 50.2334 | 1509.12
2021-06-03 22:05 | 23.2232 | 50.4497 | 1522.96
2021-06-03 22:10 | 23.2309 | 50.6665 | 1533.45
2021-06-03 22:15 | 23.2331 | 50.8679 | 1541.92
2021-06-03 22:20 | 23.2329 | 51.0483 | 1548.98
2021-06-03 22:25 | 23.2315 | 51.2073 | 1554.97
2021-06-03 22:30 | 23.2296 | 51.3466 | 1560.1
2021-06-03 22:35 | 23.2273 | 51.4681 | 1564.51
2021-06-03 22:40 | 23.2249 | 51.5738 | 1568.3
2021-06-03 22:45 | 23.2224 | 51.6658 | 1571.57
2021-06-03 22:50 | 23.2198 | 51.7458 | 1574.39
2021-06-03 22:55 | 23.2171 | 51.8154 | 1576.81
2021-06-03 23:00 | 23.1371 | 50.3703 | 1578.33
2021-06-03 23:05 | 23.0872 | 49.0473 | 1519.3
2021-06-03 23:10 | 23.0524 | 47.8662 | 1470.82
2021-06-03 23:15 | 23.0252 | 46.8256 | 1430.11
2021-06-03 23:20 | 23.0025 | 45.9152 | 1394.91
2021-06-03 23:25 | 22.9825 | 45.1217 | 1364.34
2021-06-03 23:30 | 22.9645 | 44.4317 | 1337.71
2021-06-03 23:35 | 22.9481 | 43.8325 | 1314.48
2021-06-03 23:40 | 22.933 | 43.3127 | 1294.19
2021-06-03 23:45 | 22.9189 | 42.8623 | 1276.45
2021-06-03 23:50 | 22.9059 | 42.4725 | 1260.92
2021-06-03 23:55 | 22.8937 | 42.1353 | 1247.33
2021-06-04 | 22.8825 | 41.8444 | 1235.14
2021-06-04 00:05 | 22.8721 | 41.5938 | 1224.43
2021-06-04 00:10 | 22.8623 | 41.3784 | 1215.03
2021-06-04 00:15 | 22.8531 | 41.1937 | 1206.75
2021-06-04 00:20 | 22.8445 | 41.0358 | 1199.45
2021-06-04 00:25 | 22.8364 | 40.9011 | 1193.01
2021-06-04 00:30 | 22.8287 | 40.7866 | 1187.32
2021-06-04 00:35 | 22.8214 | 40.6897 | 1182.28
2021-06-04 00:40 | 22.8145 | 40.608 | 1177.81
2021-06-04 00:45 | 22.8079 | 40.5397 | 1173.84
2021-06-04 00:50 | 22.8017 | 40.4828 | 1170.3
2021-06-04 00:55 | 22.7957 | 40.436 | 1167.15
2021-06-04 01:00 | 22.7893 | 40.3969 | 1165.44
2021-06-04 01:05 | 22.7828 | 40.3639 | 1163.89
2021-06-04 01:10 | 22.7763 | 40.3358 | 1162.51
2021-06-04 01:15 | 22.77 | 40.3118 | 1161.27
2021-06-04 01:20 | 22.7638 | 40.2912 | 1160.16
2021-06-04 01:25 | 22.7579 | 40.2735 | 1159.19
2021-06-04 01:30 | 22.752 | 40.2585 | 1158.32
2021-06-04 01:35 | 22.7462 | 40.2458 | 1157.54
2021-06-04 01:40 | 22.7406 | 40.235 | 1156.84
2021-06-04 01:45 | 22.735 | 40.2258 | 1156.22
2021-06-04 01:50 | 22.7296 | 40.2181 | 1155.65
2021-06-04 01:55 | 22.7243 | 40.2116 | 1155.15
2021-06-04 02:00 | 22.7194 | 40.2065 | 1154.23
2021-06-04 02:05 | 22.7147 | 40.2029 | 1153.41
2021-06-04 02:10 | 22.7102 | 40.2008 | 1152.66
2021-06-04 02:15 | 22.7059 | 40.1999 | 1151.99
2021-06-04 02:20 | 22.7016 | 40.2001 | 1151.36
2021-06-04 02:25 | 22.6975 | 40.2012 | 1150.79
2021-06-04 02:30 | 22.6934 | 40.2032 | 1150.26
2021-06-04 02:35 | 22.6894 | 40.2058 | 1149.76
2021-06-04 02:40 | 22.6855 | 40.2091 | 1149.3
2021-06-04 02:45 | 22.6817 | 40.2129 | 1148.87
2021-06-04 02:50 | 22.678 | 40.217 | 1148.47
2021-06-04 02:55 | 22.6743 | 40.2216 | 1148.08
2021-06-04 03:00 | 22.6707 | 40.2264 | 1147.72
2021-06-04 03:05 | 22.6672 | 40.2315 | 1147.38
2021-06-04 03:10 | 22.6637 | 40.2367 | 1147.05
2021-06-04 03:15 | 22.6603 | 40.2422 | 1146.74
2021-06-04 03:20 | 22.657 | 40.2477 | 1146.44
2021-06-04 03:25 | 22.6537 | 40.2533 | 1146.16
2021-06-04 03:30 | 22.6505 | 40.2591 | 1145.89
2021-06-04 03:35 | 22.6473 | 40.2648 | 1145.62
2021-06-04 03:40 | 22.6441 | 40.2706 | 1145.37
2021-06-04 03:45 | 22.6411 | 40.2764 | 1145.12
2021-06-04 03:50 | 22.638 | 40.2822 | 1144.88
2021-06-04 03:55 | 22.635 | 40.288 | 1144.65
2021-06-04 04:00 | 22.6317 | 40.2934 | 1144.91
2021-06-04 04:05 | 22.6284 | 40.2981 | 1145.12
2021-06-04 04:10 | 22.625 | 40.3021 | 1145.3
2021-06-04 04:15 | 22.6215 | 40.3054 | 1145.44
2021-06-04 04:20 | 22.6181 | 40.308 | 1145.57
2021-06-04 04:25 | 22.6147 | 40.3101 | 1145.68
2021-06-04 04:30 | 22.6113 | 40.3116 | 1145.77
2021-06-04 04:35 | 22.6079 | 40.3127 | 1145.86
2021-06-04 04:40 | 22.6046 | 40.3134 | 1145.93
2021-06-04 04:45 | 22.6012 | 40.3138 | 1145.99
2021-06-04 04:50 | 22.5979 | 40.3138 | 1146.04
2021-06-04 04:55 | 22.5946 | 40.3135 | 1146.09
2021-06-04 05:00 | 22.5912 | 40.3128 | 1146.42
2021-06-04 05:05 | 22.5876 | 40.3115 | 1146.71
2021-06-04 05:10 | 22.5841 | 40.3095 | 1146.97
2021-06-04 05:15 | 22.5805 | 40.307 | 1147.22
2021-06-04 05:20 | 22.5769 | 40.3039 | 1147.44
2021-06-04 05:25 | 22.5734 | 40.3004 | 1147.65
2021-06-04 05:30 | 22.5698 | 40.2965 | 1147.85
2021-06-04 05:35 | 22.5662 | 40.2922 | 1148.04
2021-06-04 05:40 | 22.5627 | 40.2876 | 1148.22
2021-06-04 05:45 | 22.5592 | 40.2827 | 1148.39
2021-06-04 05:50 | 22.5556 | 40.2776 | 1148.56
2021-06-04 05:55 | 22.5521 | 40.2722 | 1148.72
2021-06-04 06:00 | 22.5494 | 40.2676 | 1147.7
2021-06-04 06:05 | 22.547 | 40.2643 | 1146.81
2021-06-04 06:10 | 22.5448 | 40.2626 | 1146.01
2021-06-04 06:15 | 22.5428 | 40.2623 | 1145.29
2021-06-04 06:20 | 22.5409 | 40.2634 | 1144.62
2021-06-04 06:25 | 22.539 | 40.2656 | 1144.01
2021-06-04 06:30 | 22.5372 | 40.2688 | 1143.44
2021-06-04 06:35 | 22.5354 | 40.273 | 1142.9
2021-06-04 06:40 | 22.5337 | 40.2779 | 1142.4
2021-06-04 06:45 | 22.5321 | 40.2834 | 1141.92
2021-06-04 06:50 | 22.5304 | 40.2896 | 1141.48
2021-06-04 06:55 | 22.5289 | 40.2962 | 1141.05
2021-06-04 07:00 | 22.5283 | 40.3045 | 1139.19
2021-06-04 07:05 | 22.5282 | 40.315 | 1137.52
2021-06-04 07:10 | 22.5284 | 40.3279 | 1135.97
2021-06-04 07:15 | 22.5287 | 40.343 | 1134.52
2021-06-04 07:20 | 22.5292 | 40.3602 | 1133.15
2021-06-04 07:25 | 22.5299 | 40.3791 | 1131.85
2021-06-04 07:30 | 22.5306 | 40.3997 | 1130.61
2021-06-04 07:35 | 22.5314 | 40.4217 | 1129.42
2021-06-04 07:40 | 22.5323 | 40.4449 | 1128.27
2021-06-04 07:45 | 22.5333 | 40.4692 | 1127.16
2021-06-04 07:50 | 22.5344 | 40.4945 | 1126.08
2021-06-04 07:55 | 22.5355 | 40.5206 | 1125.03
2021-06-04 08:00 | 22.5359 | 40.5463 | 1125.23
2021-06-04 08:05 | 22.5361 | 40.5711 | 1125.33
2021-06-04 08:10 | 22.5361 | 40.5946 | 1125.35
2021-06-04 08:15 | 22.536 | 40.6169 | 1125.32
2021-06-04 08:20 | 22.5358 | 40.6381 | 1125.24
2021-06-04 08:25 | 22.5357 | 40.6582 | 1125.14
2021-06-04 08:30 | 22.5356 | 40.6774 | 1125
2021-06-04 08:35 | 22.5354 | 40.6958 | 1124.84
2021-06-04 08:40 | 22.5353 | 40.7135 | 1124.67
2021-06-04 08:45 | 22.5352 | 40.7305 | 1124.47
2021-06-04 08:50 | 22.535 | 40.7469 | 1124.26
2021-06-04 08:55 | 22.5349 | 40.7628 | 1124.04
2021-06-04 09:00 | 22.5356 | 40.7792 | 1122.6
2021-06-04 09:05 | 22.5367 | 40.7968 | 1121.27
2021-06-04 09:10 | 22.538 | 40.8158 | 1120.03
2021-06-04 09:15 | 22.5395 | 40.8361 | 1118.84
2021-06-04 09:20 | 22.5411 | 40.8577 | 1117.71
2021-06-04 09:25 | 22.5428 | 40.8804 | 1116.61
2021-06-04 09:30 | 22.5445 | 40.9041 | 1115.55
2021-06-04 09:35 | 22.5464 | 40.9287 | 1114.52
2021-06-04 09:40 | 22.5483 | 40.954 | 1113.51
2021-06-04 09:45 | 22.5503 | 40.9801 | 1112.53
2021-06-04 09:50 | 22.5524 | 41.0067 | 1111.56
2021-06-04 09:55 | 22.5545 | 41.034 | 1110.61
2021-06-04 10:00 | 22.7664 | 40.5318 | 1114.09
2021-06-04 10:05 | 22.8655 | 40.3044 | 1133.5
2021-06-04 10:10 | 22.9162 | 40.189 | 1144.07
2021-06-04 10:15 | 22.9431 | 40.1251 | 1150.77
2021-06-04 10:20 | 22.9584 | 40.0831 | 1155.48
2021-06-04 10:25 | 22.9679 | 40.05 | 1159.17
2021-06-04 10:30 | 22.9742 | 40.0197 | 1162.31
2021-06-04 10:35 | 22.9785 | 39.9897 | 1165.1
2021-06-04 10:40 | 22.9816 | 39.9587 | 1167.66
2021-06-04 10:45 | 22.9837 | 39.9263 | 1170.06
2021-06-04 10:50 | 22.9851 | 39.8925 | 1172.33
2021-06-04 10:55 | 23.164 | 40.1876 | 1174.51
2021-06-04 11:00 | 23.2272 | 40.0661 | 1211.17
2021-06-04 11:05 | 23.2638 | 40.0034 | 1218.73
2021-06-04 11:10 | 23.2868 | 39.9677 | 1224.1
2021-06-04 11:15 | 23.3026 | 39.9435 | 1228.26
2021-06-04 11:20 | 23.3145 | 39.9234 | 1231.73
2021-06-04 11:25 | 23.3241 | 39.9038 | 1234.77
2021-06-04 11:30 | 23.3323 | 39.8831 | 1237.52
2021-06-04 11:35 | 23.3395 | 39.8609 | 1240.06
2021-06-04 11:40 | 23.3458 | 39.8371 | 1242.44
2021-06-04 11:45 | 23.3516 | 39.8114 | 1244.68
2021-06-04 11:50 | 23.3568 | 39.7842 | 1246.82
2021-06-04 11:55 | 23.3615 | 39.7554 | 1248.85
2021-06-04 12:00 | 23.3091 | 39.8011 | 1248.29
2021-06-04 12:05 | 23.2859 | 39.7864 | 1241.44
2021-06-04 12:10 | 23.2761 | 39.7489 | 1237.16
2021-06-04 12:15 | 23.2728 | 39.7041 | 1234.2
2021-06-04 12:20 | 23.2728 | 39.6593 | 1232.01
2021-06-04 12:25 | 23.2743 | 39.6175 | 1230.28
2021-06-04 12:30 | 23.2784 | 39.5927 | 1228.87
2021-06-04 12:35 | 23.2822 | 39.5717 | 1228.35
2021-06-04 12:40 | 23.286 | 39.5535 | 1227.9
2021-06-04 12:45 | 23.2897 | 39.5376 | 1227.51
2021-06-04 12:50 | 23.2935 | 39.5235 | 1227.2
2021-06-04 12:55 | 23.2974 | 39.5109 | 1226.94
2021-06-04 13:00 | 23.3011 | 39.4989 | 1227.1
2021-06-04 13:05 | 23.3047 | 39.4875 | 1227.26
2021-06-04 13:10 | 23.3082 | 39.4766 | 1227.44
2021-06-04 13:15 | 23.3118 | 39.4662 | 1227.63
2021-06-04 13:20 | 23.3155 | 39.456 | 1227.83
2021-06-04 13:25 | 23.3191 | 39.446 | 1228.04
2021-06-04 13:30 | 23.3208 | 39.4233 | 1228.27
2021-06-04 13:35 | 23.3236 | 39.4007 | 1227.83
2021-06-04 13:40 | 23.3267 | 39.3791 | 1227.55
2021-06-04 13:45 | 23.3301 | 39.359 | 1227.37
2021-06-04 13:50 | 23.3337 | 39.3401 | 1227.26
2021-06-04 13:55 | 23.3373 | 39.3224 | 1227.21
2021-06-04 14:00 | 23.3481 | 39.4749 | 1227.33
2021-06-04 14:05 | 23.3561 | 39.611 | 1233.48
2021-06-04 14:10 | 23.3628 | 39.7302 | 1238.74
2021-06-04 14:15 | 23.3687 | 39.8335 | 1243.32
2021-06-04 14:20 | 23.3744 | 39.9222 | 1247.33
2021-06-04 14:25 | 23.3798 | 39.9984 | 1250.88
2021-06-04 14:30 | 23.3851 | 40.0632 | 1254.01
2021-06-04 14:35 | 23.3902 | 40.1184 | 1256.8
2021-06-04 14:40 | 23.3952 | 40.1647 | 1259.27
2021-06-04 14:45 | 23.4002 | 40.2037 | 1261.49
2021-06-04 14:50 | 23.4051 | 40.2361 | 1263.48
2021-06-04 14:55 | 23.41 | 40.2626 | 1265.26
2021-06-04 15:00 | 23.1987 | 40.8139 | 1266.79
2021-06-04 15:05 | 23.1031 | 41.0739 | 1251.36
2021-06-04 15:10 | 23.0565 | 41.2074 | 1244.63
2021-06-04 15:15 | 23.0332 | 41.2796 | 1241.53
2021-06-04 15:20 | 23.0204 | 41.3228 | 1240.13
2021-06-04 15:25 | 23.0128 | 41.3513 | 1239.49
2021-06-04 15:30 | 23.0079 | 41.3717 | 1239.19
2021-06-04 15:35 | 23.0045 | 41.3868 | 1239.06
2021-06-04 15:40 | 23.0021 | 41.3987 | 1239.01
2021-06-04 15:45 | 23.0003 | 41.4081 | 1239.01
2021-06-04 15:50 | 22.999 | 41.4155 | 1239.03
2021-06-04 15:55 | 22.9981 | 41.4213 | 1239.06
2021-06-04 16:00 | 23.2125 | 40.9303 | 1239.14
2021-06-04 16:05 | 23.3132 | 40.7252 | 1257.08
2021-06-04 16:10 | 23.3661 | 40.636 | 1266.23
2021-06-04 16:15 | 23.3959 | 40.5998 | 1271.58
2021-06-04 16:20 | 23.4148 | 40.5862 | 1275.03
2021-06-04 16:25 | 23.4284 | 40.5819 | 1277.52
2021-06-04 16:30 | 23.4393 | 40.5809 | 1279.49
2021-06-04 16:35 | 23.4485 | 40.5808 | 1281.14
2021-06-04 16:40 | 23.4568 | 40.5802 | 1282.58
2021-06-04 16:45 | 23.4645 | 40.5786 | 1283.87
2021-06-04 16:50 | 23.4717 | 40.5761 | 1285.04
2021-06-04 16:55 | 23.4785 | 40.5726 | 1286.12
2021-06-04 17:00 | 23.4848 | 40.5679 | 1287.45
2021-06-04 17:05 | 23.4907 | 40.5621 | 1288.68
2021-06-04 17:10 | 23.4963 | 40.5552 | 1289.82
2021-06-04 17:15 | 23.5017 | 40.5471 | 1290.87
2021-06-04 17:20 | 23.5069 | 40.5382 | 1291.87
2021-06-04 17:25 | 23.5118 | 40.5285 | 1292.8
2021-06-04 17:30 | 23.594 | 41.0449 | 1293.68
2021-06-04 17:35 | 23.6398 | 41.5578 | 1321.87
2021-06-04 17:40 | 23.6689 | 42.0309 | 1344.6
2021-06-04 17:45 | 23.6895 | 42.4543 | 1363.67
2021-06-04 17:50 | 23.7056 | 42.8268 | 1380
2021-06-04 17:55 | 23.7191 | 43.1517 | 1394.15
2021-06-04 18:00 | 23.7312 | 43.4335 | 1406.34
2021-06-04 18:05 | 23.7422 | 43.6774 | 1417.02
2021-06-04 18:10 | 23.7523 | 43.888 | 1426.38
2021-06-04 18:15 | 23.7617 | 44.0694 | 1434.62
2021-06-04 18:20 | 23.7704 | 44.2256 | 1441.88
2021-06-04 18:25 | 23.7786 | 44.3597 | 1448.28
2021-06-04 18:30 | 23.7864 | 44.4745 | 1453.92
2021-06-04 18:35 | 23.7936 | 44.5728 | 1458.92
2021-06-04 18:40 | 23.8004 | 44.6567 | 1463.33
2021-06-04 18:45 | 23.8069 | 44.728 | 1467.25
2021-06-04 18:50 | 23.813 | 44.7885 | 1470.73
2021-06-04 18:55 | 23.8187 | 44.8397 | 1473.82
2021-06-04 19:00 | 23.8243 | 44.883 | 1476.29
2021-06-04 19:05 | 23.8296 | 44.9196 | 1478.5
2021-06-04 19:10 | 23.8347 | 44.9504 | 1480.47
2021-06-04 19:15 | 23.8396 | 44.9763 | 1482.23
2021-06-04 19:20 | 23.8442 | 44.9979 | 1483.81
2021-06-04 19:25 | 23.8487 | 45.0159 | 1485.23
2021-06-04 19:30 | 23.8529 | 45.0308 | 1486.5
2021-06-04 19:35 | 23.8569 | 45.043 | 1487.64
2021-06-04 19:40 | 23.8608 | 45.053 | 1488.67
2021-06-04 19:45 | 23.8644 | 45.0609 | 1489.61
2021-06-04 19:50 | 23.8678 | 45.0672 | 1490.45
2021-06-04 19:55 | 23.8711 | 45.0721 | 1491.22
2021-06-04 20:00 | 23.9509 | 45.603 | 1492.19
2021-06-04 20:05 | 23.9929 | 46.1278 | 1521.6
2021-06-04 20:10 | 24.0178 | 46.6052 | 1544.87
2021-06-04 20:15 | 24.0342 | 47.0255 | 1563.99
2021-06-04 20:20 | 24.0462 | 47.3888 | 1579.99
2021-06-04 20:25 | 24.0556 | 47.6998 | 1593.51
2021-06-04 20:30 | 23.7922 | 48.4282 | 1597.27
2021-06-04 20:35 | 23.5703 | 49.0058 | 1578.06
2021-06-04 20:40 | 23.497 | 49.1564 | 1564.87
2021-06-04 20:45 | 23.4593 | 49.2045 | 1557.52
2021-06-04 20:50 | 23.4373 | 49.2108 | 1553
2021-06-04 20:55 | 23.4226 | 49.2008 | 1549.83
2021-06-04 21:00 | 23.4117 | 49.185 | 1547.28
2021-06-04 21:05 | 23.4028 | 49.1682 | 1545.18
2021-06-04 21:10 | 23.395 | 49.1523 | 1543.39
2021-06-04 21:15 | 23.3881 | 49.1383 | 1541.82
2021-06-04 21:20 | 23.3817 | 49.126 | 1540.43
2021-06-04 21:25 | 23.3758 | 49.1155 | 1539.2
2021-06-04 21:30 | 23.2637 | 49.4237 | 1538.09
2021-06-04 21:35 | 23.2112 | 49.5497 | 1528.87
2021-06-04 21:40 | 23.1827 | 49.604 | 1524.1
2021-06-04 21:45 | 23.1652 | 49.6268 | 1521.17
2021-06-04 21:50 | 23.1527 | 49.6369 | 1519.14
2021-06-04 21:55 | 23.1425 | 49.6419 | 1517.55
2021-06-04 22:00 | 23.192 | 49.8184 | 1516.06
2021-06-04 22:05 | 23.2124 | 50.0435 | 1529.51
2021-06-04 22:10 | 23.2209 | 50.2687 | 1539.6
2021-06-04 22:15 | 23.224 | 50.4782 | 1547.74
2021-06-04 22:20 | 23.2247 | 50.6667 | 1554.51
2021-06-04 22:25 | 23.2243 | 50.8339 | 1560.27
2021-06-04 22:30 | 23.2233 | 50.9812 | 1565.2
2021-06-04 22:35 | 23.222 | 51.1106 | 1569.45
2021-06-04 22:40 | 23.2204 | 51.2242 | 1573.12
2021-06-04 22:45 | 23.2187 | 51.3238 | 1576.28
2021-06-04 22:50 | 23.2169 | 51.4113 | 1579.01
2021-06-04 22:55 | 23.215 | 51.488 | 1581.36
2021-06-04 23:00 | 23.1357 | 50.0481 | 1582.89
2021-06-04 23:05 | 23.0847 | 48.7298 | 1526.68
2021-06-04 23:10 | 23.049 | 47.5506 | 1479.14
2021-06-04 23:15 | 23.0215 | 46.5102 | 1438.43
2021-06-04 23:20 | 22.9985 | 45.5993 | 1403.27
2021-06-04 23:25 | 22.9785 | 44.8049 | 1372.74
2021-06-04 23:30 | 22.9605 | 44.1139 | 1346.15
2021-06-04 23:35 | 22.9441 | 43.5135 | 1322.94
2021-06-04 23:40 | 22.9291 | 42.9925 | 1302.66
2021-06-04 23:45 | 22.9151 | 42.541 | 1284.93
2021-06-04 23:50 | 22.9021 | 42.1501 | 1269.4
2021-06-04 23:55 | 22.89 | 41.8119 | 1255.79
2021-06-05 | 22.8787 | 41.5198 | 1243.87
2021-06-05 00:05 | 22.868 | 41.2677 | 1233.41
2021-06-05 00:10 | 22.858 | 41.0505 | 1224.21
2021-06-05 00:15 | 22.8486 | 40.8637 | 1216.12
2021-06-05 00:20 | 22.8397 | 40.7033 | 1208.99
2021-06-05 00:25 | 22.8312 | 40.5659 | 1202.71
2021-06-05 00:30 | 22.8232 | 40.4486 | 1197.16
2021-06-05 00:35 | 22.8156 | 40.3487 | 1192.25
2021-06-05 00:40 | 22.8083 | 40.2639 | 1187.9
2021-06-05 00:45 | 22.8014 | 40.1922 | 1184.04
2021-06-05 00:50 | 22.7948 | 40.132 | 1180.61
2021-06-05 00:55 | 22.7885 | 40.0817 | 1177.55
2021-06-05 01:00 | 22.7818 | 40.0392 | 1175.79
2021-06-05 01:05 | 22.775 | 40.0028 | 1174.19
2021-06-05 01:10 | 22.7684 | 39.9716 | 1172.76
2021-06-05 01:15 | 22.7618 | 39.9447 | 1171.49
2021-06-05 01:20 | 22.7556 | 39.9212 | 1170.36
2021-06-05 01:25 | 22.7494 | 39.9009 | 1169.37
2021-06-05 01:30 | 22.7434 | 39.8834 | 1168.48
2021-06-05 01:35 | 22.7374 | 39.8683 | 1167.69
2021-06-05 01:40 | 22.7316 | 39.8552 | 1166.98
2021-06-05 01:45 | 22.7259 | 39.8439 | 1166.35
2021-06-05 01:50 | 22.7203 | 39.8341 | 1165.78
2021-06-05 01:55 | 22.7149 | 39.8256 | 1165.27
2021-06-05 02:00 | 22.7099 | 39.8187 | 1164.22
2021-06-05 02:05 | 22.7052 | 39.8136 | 1163.28
2021-06-05 02:10 | 22.7006 | 39.8102 | 1162.43
2021-06-05 02:15 | 22.6962 | 39.8083 | 1161.66
2021-06-05 02:20 | 22.692 | 39.8076 | 1160.95
2021-06-05 02:25 | 22.6878 | 39.8081 | 1160.3
2021-06-05 02:30 | 22.6837 | 39.8096 | 1159.7
2021-06-05 02:35 | 22.6798 | 39.812 | 1159.14
2021-06-05 02:40 | 22.6759 | 39.815 | 1158.62
2021-06-05 02:45 | 22.6721 | 39.8186 | 1158.14
2021-06-05 02:50 | 22.6683 | 39.8227 | 1157.68
2021-06-05 02:55 | 22.6647 | 39.8273 | 1157.25
2021-06-05 03:00 | 22.6615 | 39.8327 | 1156.27
2021-06-05 03:05 | 22.6585 | 39.8391 | 1155.37
2021-06-05 03:10 | 22.6558 | 39.8465 | 1154.54
2021-06-05 03:15 | 22.6531 | 39.8549 | 1153.77
2021-06-05 03:20 | 22.6505 | 39.8642 | 1153.04
2021-06-05 03:25 | 22.6481 | 39.8742 | 1152.36
2021-06-05 03:30 | 22.6457 | 39.8848 | 1151.7
2021-06-05 03:35 | 22.6433 | 39.896 | 1151.08
2021-06-05 03:40 | 22.6411 | 39.9076 | 1150.48
2021-06-05 03:45 | 22.6389 | 39.9196 | 1149.91
2021-06-05 03:50 | 22.6368 | 39.9319 | 1149.36
2021-06-05 03:55 | 22.6348 | 39.9444 | 1148.83
2021-06-05 04:00 | 22.633 | 39.9575 | 1147.98
2021-06-05 04:05 | 22.6313 | 39.9711 | 1147.18
2021-06-05 04:10 | 22.6298 | 39.9854 | 1146.43
2021-06-05 04:15 | 22.6284 | 40.0003 | 1145.71
2021-06-05 04:20 | 22.627 | 40.0156 | 1145.02
2021-06-05 04:25 | 22.6257 | 40.0313 | 1144.36
2021-06-05 04:30 | 22.6245 | 40.0474 | 1143.73
2021-06-05 04:35 | 22.6233 | 40.0638 | 1143.11
2021-06-05 04:40 | 22.6222 | 40.0804 | 1142.52
2021-06-05 04:45 | 22.6211 | 40.0972 | 1141.94
2021-06-05 04:50 | 22.6201 | 40.1141 | 1141.38
2021-06-05 04:55 | 22.6191 | 40.1312 | 1140.83
2021-06-05 05:00 | 22.6173 | 40.1473 | 1141.51
2021-06-05 05:05 | 22.6153 | 40.1618 | 1142.06
2021-06-05 05:10 | 22.6131 | 40.1747 | 1142.52
2021-06-05 05:15 | 22.6107 | 40.1859 | 1142.91
2021-06-05 05:20 | 22.6084 | 40.1956 | 1143.23
2021-06-05 05:25 | 22.606 | 40.204 | 1143.51
2021-06-05 05:30 | 22.6037 | 40.2112 | 1143.75
2021-06-05 05:35 | 22.6013 | 40.2174 | 1143.95
2021-06-05 05:40 | 22.5989 | 40.2227 | 1144.13
2021-06-05 05:45 | 22.5965 | 40.2272 | 1144.27
2021-06-05 05:50 | 22.5941 | 40.231 | 1144.4
2021-06-05 05:55 | 22.5918 | 40.2342 | 1144.5
2021-06-05 06:00 | 22.5905 | 40.2382 | 1142.88
2021-06-05 06:05 | 22.5898 | 40.244 | 1141.45
2021-06-05 06:10 | 22.5893 | 40.2518 | 1140.14
2021-06-05 06:15 | 22.5891 | 40.2616 | 1138.93
2021-06-05 06:20 | 22.589 | 40.2731 | 1137.8
2021-06-05 06:25 | 22.5889 | 40.2862 | 1136.73
2021-06-05 06:30 | 22.589 | 40.3008 | 1135.73
2021-06-05 06:35 | 22.5891 | 40.3165 | 1134.77
2021-06-05 06:40 | 22.5893 | 40.3332 | 1133.85
2021-06-05 06:45 | 22.5895 | 40.3509 | 1132.98
2021-06-05 06:50 | 22.5899 | 40.3693 | 1132.13
2021-06-05 06:55 | 22.5902 | 40.3884 | 1131.32
2021-06-05 07:00 | 22.5906 | 40.408 | 1130.57
2021-06-05 07:05 | 22.5911 | 40.4279 | 1129.84
2021-06-05 07:10 | 22.5916 | 40.4481 | 1129.13
2021-06-05 07:15 | 22.5922 | 40.4686 | 1128.42
2021-06-05 07:20 | 22.5928 | 40.4894 | 1127.73
2021-06-05 07:25 | 22.5935 | 40.5104 | 1127.04
2021-06-05 07:30 | 22.5942 | 40.5316 | 1126.36
2021-06-05 07:35 | 22.595 | 40.5529 | 1125.69
2021-06-05 07:40 | 22.5958 | 40.5744 | 1125.03
2021-06-05 07:45 | 22.5966 | 40.596 | 1124.37
2021-06-05 07:50 | 22.5975 | 40.6178 | 1123.71
2021-06-05 07:55 | 22.5984 | 40.6396 | 1123.06
2021-06-05 08:00 | 22.5976 | 40.6593 | 1125.23
2021-06-05 08:05 | 22.5959 | 40.6753 | 1127.1
2021-06-05 08:10 | 22.5937 | 40.6874 | 1128.77
2021-06-05 08:15 | 22.5913 | 40.6955 | 1130.28
2021-06-05 08:20 | 22.5887 | 40.7002 | 1131.68
2021-06-05 08:25 | 22.5859 | 40.7016 | 1132.98
2021-06-05 08:30 | 22.583 | 40.7002 | 1134.19
2021-06-05 08:35 | 22.58 | 40.6961 | 1135.34
2021-06-05 08:40 | 22.5769 | 40.6898 | 1136.42
2021-06-05 08:45 | 22.5737 | 40.6814 | 1137.46
2021-06-05 08:50 | 22.5705 | 40.6711 | 1138.46
2021-06-05 08:55 | 22.5671 | 40.6592 | 1139.42
2021-06-05 09:00 | 22.5646 | 40.6469 | 1138.91
2021-06-05 09:05 | 22.5625 | 40.6352 | 1138.52
2021-06-05 09:10 | 22.5605 | 40.6243 | 1138.21
2021-06-05 09:15 | 22.5587 | 40.6143 | 1137.97
2021-06-05 09:20 | 22.5569 | 40.6051 | 1137.78
2021-06-05 09:25 | 22.5552 | 40.5966 | 1137.63
2021-06-05 09:30 | 22.5535 | 40.5887 | 1137.52
2021-06-05 09:35 | 22.5518 | 40.5813 | 1137.44
2021-06-05 09:40 | 22.5501 | 40.5743 | 1137.39
2021-06-05 09:45 | 22.5485 | 40.5673 | 1137.37
2021-06-05 09:50 | 22.5469 | 40.5609 | 1137.38
2021-06-05 09:55 | 22.5453 | 40.5544 | 1137.4
2021-06-05 10:00 | 22.7563 | 40.0285 | 1137.41
2021-06-05 10:05 | 22.8549 | 39.7818 | 1153.92
2021-06-05 10:10 | 22.906 | 39.6512 | 1161.77
2021-06-05 10:15 | 22.9341 | 39.5767 | 1165.97
2021-06-05 10:20 | 22.9512 | 39.5284 | 1168.4
2021-06-05 10:25 | 22.9628 | 39.4933 | 1169.99
2021-06-05 10:30 | 22.9715 | 39.465 | 1171.16
2021-06-05 10:35 | 22.9785 | 39.4406 | 1172.1
2021-06-05 10:40 | 22.9845 | 39.4185 | 1172.92
2021-06-05 10:45 | 22.9898 | 39.3979 | 1173.67
2021-06-05 10:50 | 22.9945 | 39.3786 | 1174.36
2021-06-05 10:55 | 23.1767 | 39.6962 | 1175.01
2021-06-05 11:00 | 23.2426 | 39.596 | 1210.89
2021-06-05 11:05 | 23.2819 | 39.5545 | 1217.63
2021-06-05 11:10 | 23.3078 | 39.5402 | 1222.17
2021-06-05 11:15 | 23.3265 | 39.5376 | 1225.51
2021-06-05 11:20 | 23.3415 | 39.5394 | 1228.16
2021-06-05 11:25 | 23.3542 | 39.5422 | 1230.38
2021-06-05 11:30 | 23.3657 | 39.5444 | 1232.31
2021-06-05 11:35 | 23.3761 | 39.5456 | 1234.03
2021-06-05 11:40 | 23.3858 | 39.5456 | 1235.57
2021-06-05 11:45 | 23.3949 | 39.5443 | 1236.98
2021-06-05 11:50 | 23.4036 | 39.5419 | 1238.28
2021-06-05 11:55 | 23.4118 | 39.5385 | 1239.47
2021-06-05 12:00 | 23.3613 | 39.6067 | 1240.62
2021-06-05 12:05 | 23.3393 | 39.6125 | 1235.19
2021-06-05 12:10 | 23.3301 | 39.5927 | 1232.13
2021-06-05 12:15 | 23.3272 | 39.5629 | 1230.23
2021-06-05 12:20 | 23.3273 | 39.5305 | 1228.97
2021-06-05 12:25 | 23.3289 | 39.4987 | 1228.07
2021-06-05 12:30 | 23.333 | 39.4828 | 1227.41
2021-06-05 12:35 | 23.3366 | 39.4687 | 1227.59
2021-06-05 12:40 | 23.34 | 39.4557 | 1227.76
2021-06-05 12:45 | 23.3434 | 39.4435 | 1227.93
2021-06-05 12:50 | 23.3467 | 39.4318 | 1228.12
2021-06-05 12:55 | 23.35 | 39.4205 | 1228.32
2021-06-05 13:00 | 23.3557 | 39.414 | 1224.84
2021-06-05 13:05 | 23.3625 | 39.4131 | 1221.83
2021-06-05 13:10 | 23.37 | 39.4178 | 1219.16
2021-06-05 13:15 | 23.3779 | 39.4281 | 1216.75
2021-06-05 13:20 | 23.386 | 39.4432 | 1214.56
2021-06-05 13:25 | 23.3943 | 39.4626 | 1212.55
2021-06-05 13:30 | 23.4009 | 39.4677 | 1210.7
2021-06-05 13:35 | 23.4085 | 39.4763 | 1208.17
2021-06-05 13:40 | 23.4165 | 39.4889 | 1205.89
2021-06-05 13:45 | 23.4249 | 39.5052 | 1203.8
2021-06-05 13:50 | 23.4335 | 39.525 | 1201.87
2021-06-05 13:55 | 23.4422 | 39.5479 | 1200.07
2021-06-05 14:00 | 23.4581 | 39.7422 | 1198.16
2021-06-05 14:05 | 23.4716 | 39.9215 | 1202.44
2021-06-05 14:10 | 23.4838 | 40.0856 | 1205.92
2021-06-05 14:15 | 23.4953 | 40.2351 | 1208.77
2021-06-05 14:20 | 23.5066 | 40.3714 | 1211.12
2021-06-05 14:25 | 23.5176 | 40.496 | 1213.04
2021-06-05 14:30 | 23.5285 | 40.6104 | 1214.6
2021-06-05 14:35 | 23.5393 | 40.7158 | 1215.84
2021-06-05 14:40 | 23.55 | 40.8132 | 1216.81
2021-06-05 14:45 | 23.5606 | 40.9037 | 1217.53
2021-06-05 14:50 | 23.5712 | 40.9882 | 1218.05
2021-06-05 14:55 | 23.5818 | 41.0675 | 1218.4
2021-06-05 15:00 | 23.3727 | 41.6832 | 1221.76
2021-06-05 15:05 | 23.2779 | 41.9999 | 1207.92
2021-06-05 15:10 | 23.2318 | 42.1822 | 1202.74
2021-06-05 15:15 | 23.2089 | 42.2965 | 1200.98
2021-06-05 15:20 | 23.1968 | 42.3761 | 1200.63
2021-06-05 15:25 | 23.1898 | 42.4366 | 1200.86
2021-06-05 15:30 | 23.1855 | 42.4855 | 1201.28
2021-06-05 15:35 | 23.1826 | 42.5263 | 1201.74
2021-06-05 15:40 | 23.1807 | 42.5613 | 1202.19
2021-06-05 15:45 | 23.1793 | 42.5917 | 1202.6
2021-06-05 15:50 | 23.1783 | 42.6184 | 1202.95
2021-06-05 15:55 | 23.1778 | 42.6418 | 1203.26
2021-06-05 16:00 | 23.3926 | 42.1479 | 1204.9
2021-06-05 16:05 | 23.4944 | 41.9444 | 1223.45
2021-06-05 16:10 | 23.5476 | 41.8589 | 1233.66
2021-06-05 16:15 | 23.577 | 41.827 | 1240.12
2021-06-05 16:20 | 23.595 | 41.8171 | 1244.61
2021-06-05 16:25 | 23.6073 | 41.8154 | 1248.06
2021-06-05 16:30 | 23.6166 | 41.8156 | 1250.88
2021-06-05 16:35 | 23.6241 | 41.8153 | 1253.3
2021-06-05 16:40 | 23.6306 | 41.8132 | 1255.43
2021-06-05 16:45 | 23.6364 | 41.8089 | 1257.34
2021-06-05 16:50 | 23.6417 | 41.8027 | 1259.07
2021-06-05 16:55 | 23.6465 | 41.7946 | 1260.66
2021-06-05 17:00 | 23.6513 | 41.7849 | 1261.86
2021-06-05 17:05 | 23.6558 | 41.7741 | 1262.99
2021-06-05 17:10 | 23.6601 | 41.7625 | 1264.06
2021-06-05 17:15 | 23.6642 | 41.75 | 1265.06
2021-06-05 17:20 | 23.668 | 41.7371 | 1266.05
2021-06-05 17:25 | 23.6716 | 41.7237 | 1266.99
2021-06-05 17:30 | 23.7518 | 42.2297 | 1267.88
2021-06-05 17:35 | 23.7959 | 42.733 | 1297.06
2021-06-05 17:40 | 23.823 | 43.1969 | 1320.82
2021-06-05 17:45 | 23.8414 | 43.6111 | 1340.73
2021-06-05 17:50 | 23.8554 | 43.9745 | 1357.72
2021-06-05 17:55 | 23.8668 | 44.2901 | 1372.39
2021-06-05 18:00 | 23.8772 | 44.5628 | 1384.31
2021-06-05 18:05 | 23.8868 | 44.7983 | 1394.71
2021-06-05 18:10 | 23.8957 | 45.0015 | 1403.78
2021-06-05 18:15 | 23.9041 | 45.1764 | 1411.71
2021-06-05 18:20 | 23.912 | 45.327 | 1418.64
2021-06-05 18:25 | 23.9194 | 45.4566 | 1424.71
2021-06-05 18:30 | 23.9264 | 45.5679 | 1430.03
2021-06-05 18:35 | 23.9331 | 45.6635 | 1434.7
2021-06-05 18:40 | 23.9394 | 45.7454 | 1438.79
2021-06-05 18:45 | 23.9454 | 45.8155 | 1442.4
2021-06-05 18:50 | 23.951 | 45.8758 | 1445.57
2021-06-05 18:55 | 23.9564 | 45.9273 | 1448.36
2021-06-05 19:00 | 23.961 | 45.9708 | 1451.6
2021-06-05 19:05 | 23.9651 | 46.0069 | 1454.47
2021-06-05 19:10 | 23.9688 | 46.0365 | 1457.01
2021-06-05 19:15 | 23.9723 | 46.0602 | 1459.27
2021-06-05 19:20 | 23.9755 | 46.079 | 1461.3
2021-06-05 19:25 | 23.9785 | 46.0934 | 1463.13
2021-06-05 19:30 | 23.9812 | 46.1041 | 1464.77
2021-06-05 19:35 | 23.9838 | 46.1116 | 1466.26
2021-06-05 19:40 | 23.9861 | 46.1163 | 1467.61
2021-06-05 19:45 | 23.9883 | 46.1187 | 1468.83
2021-06-05 19:50 | 23.9903 | 46.1192 | 1469.95
2021-06-05 19:55 | 23.9922 | 46.118 | 1470.98
2021-06-05 20:00 | 24.0614 | 47.0933 | 1472.05
2021-06-05 20:05 | 24.0987 | 47.9774 | 1516.08
2021-06-05 20:10 | 24.1212 | 48.7499 | 1552.02
2021-06-05 20:15 | 24.1361 | 49.4135 | 1581.92
2021-06-05 20:20 | 24.1468 | 49.9778 | 1607.01
2021-06-05 20:25 | 24.155 | 50.4547 | 1628.16
2021-06-05 20:30 | 23.8969 | 51.0181 | 1636.66
2021-06-05 20:35 | 23.6758 | 51.3414 | 1613.07
2021-06-05 20:40 | 23.6006 | 51.3113 | 1593.69
2021-06-05 20:45 | 23.5605 | 51.1986 | 1580.61
2021-06-05 20:50 | 23.5363 | 51.0628 | 1570.96
2021-06-05 20:55 | 23.5195 | 50.9278 | 1563.32
2021-06-05 21:00 | 23.5069 | 50.8024 | 1556.66
2021-06-05 21:05 | 23.4965 | 50.6898 | 1551
2021-06-05 21:10 | 23.4874 | 50.5903 | 1546.13
2021-06-05 21:15 | 23.4792 | 50.5033 | 1541.91
2021-06-05 21:20 | 23.4716 | 50.4274 | 1538.22
2021-06-05 21:25 | 23.4646 | 50.3615 | 1535.01
2021-06-05 21:30 | 23.351 | 50.6299 | 1532.19
2021-06-05 21:35 | 23.2969 | 50.7178 | 1521.86
2021-06-05 21:40 | 23.2669 | 50.7367 | 1515.91
2021-06-05 21:45 | 23.2482 | 50.7273 | 1511.88
2021-06-05 21:50 | 23.2346 | 50.7085 | 1508.88
2021-06-05 21:55 | 23.2235 | 50.6878 | 1506.45
2021-06-05 22:00 | 23.2718 | 50.8383 | 1504.4
2021-06-05 22:05 | 23.2911 | 51.041 | 1517.7
2021-06-05 22:10 | 23.2984 | 51.2462 | 1527.76
2021-06-05 22:15 | 23.3003 | 51.4377 | 1535.88
2021-06-05 22:20 | 23.2998 | 51.6096 | 1542.64
2021-06-05 22:25 | 23.2981 | 51.7614 | 1548.38
2021-06-05 22:30 | 23.2959 | 51.8943 | 1553.29
2021-06-05 22:35 | 23.2934 | 52.0103 | 1557.52
2021-06-05 22:40 | 23.2907 | 52.1112 | 1561.17
2021-06-05 22:45 | 23.2879 | 52.199 | 1564.32
2021-06-05 22:50 | 23.2851 | 52.2752 | 1567.03
2021-06-05 22:55 | 23.2822 | 52.3414 | 1569.38
2021-06-05 23:00 | 23.2027 | 50.8923 | 1571.9
2021-06-05 23:05 | 23.1519 | 49.5653 | 1514.13
2021-06-05 23:10 | 23.1167 | 48.3789 | 1465.32
2021-06-05 23:15 | 23.0896 | 47.3328 | 1423.62
2021-06-05 23:20 | 23.0671 | 46.4176 | 1387.71
2021-06-05 23:25 | 23.0474 | 45.6199 | 1356.67
2021-06-05 23:30 | 23.0297 | 44.9264 | 1329.75
2021-06-05 23:35 | 23.0129 | 44.3235 | 1307.21
2021-06-05 23:40 | 22.9967 | 43.799 | 1288.09
2021-06-05 23:45 | 22.9812 | 43.3424 | 1271.39
2021-06-05 23:50 | 22.9666 | 42.9447 | 1256.8
2021-06-05 23:55 | 22.9528 | 42.598 | 1244.08
#REF! | 22.6649 | 56.8484 | 1691.27
#REF! | 22.7341 | 54.4666 | 1627.83
#REF! | 22.764 | 52.5141 | 1567.25
#REF! | 22.7758 | 50.8717 | 1512.42
#REF! | 22.7796 | 49.4701 | 1463.75
#REF! | 22.7802 | 48.2651 | 1421.02
#REF! | 22.7794 | 47.2256 | 1383.7
#REF! | 22.778 | 46.3276 | 1351.25
#REF! | 22.7757 | 45.5509 | 1324.17
#REF! | 22.7733 | 44.878 | 1300.45
#REF! | 22.7709 | 44.295 | 1279.7
#REF! | 22.7687 | 43.7898 | 1261.56
#REF! | 22.7662 | 43.3516 | 1246.7
#REF! | 22.7635 | 42.971 | 1233.71
#REF! | 22.7609 | 42.6404 | 1222.36
#REF! | 22.7584 | 42.3529 | 1212.46
#REF! | 22.756 | 42.1032 | 1203.81
#REF! | 22.7537 | 41.8862 | 1196.27
#REF! | 22.7515 | 41.6978 | 1189.69
#REF! | 22.7494 | 41.5343 | 1183.94
#REF! | 22.7474 | 41.3924 | 1178.91
#REF! | 22.7454 | 41.2694 | 1174.52
#REF! | 22.7434 | 41.1628 | 1170.68
#REF! | 22.7415 | 41.0706 | 1167.32
#REF! | 22.7391 | 40.9903 | 1165.16
#REF! | 22.7365 | 40.9198 | 1163.26
#REF! | 22.7337 | 40.8577 | 1161.61
#REF! | 22.7309 | 40.8029 | 1160.18
#REF! | 22.7281 | 40.7543 | 1158.95
#REF! | 22.7252 | 40.7112 | 1157.89
#REF! | 22.7224 | 40.6728 | 1156.98
#REF! | 22.7194 | 40.6386 | 1156.2
#REF! | 22.7165 | 40.608 | 1155.53
#REF! | 22.7135 | 40.5806 | 1154.96
#REF! | 22.7105 | 40.5559 | 1154.47
#REF! | 22.7075 | 40.5337 | 1154.06
#REF! | 22.7047 | 40.5141 | 1153.17
#REF! | 22.7022 | 40.497 | 1152.4
#REF! | 22.6997 | 40.4823 | 1151.73
#REF! | 22.6972 | 40.4697 | 1151.13
#REF! | 22.6947 | 40.4591 | 1150.6
#REF! | 22.6923 | 40.4501 | 1150.12
#REF! | 22.6898 | 40.4426 | 1149.7
#REF! | 22.6874 | 40.4363 | 1149.31
#REF! | 22.6849 | 40.4312 | 1148.97
#REF! | 22.6824 | 40.4271 | 1148.65
#REF! | 22.68 | 40.4238 | 1148.36
#REF! | 22.6775 | 40.4213 | 1148.09
#REF! | 22.6752 | 40.4196 | 1147.52
#REF! | 22.6731 | 40.419 | 1147
#REF! | 22.6709 | 40.4193 | 1146.52
#REF! | 22.6689 | 40.4204 | 1146.08
#REF! | 22.6668 | 40.4224 | 1145.67
#REF! | 22.6648 | 40.425 | 1145.28
#REF! | 22.6627 | 40.4282 | 1144.92
#REF! | 22.6607 | 40.432 | 1144.58
#REF! | 22.6587 | 40.4362 | 1144.25
#REF! | 22.6567 | 40.4407 | 1143.94
#REF! | 22.6547 | 40.4456 | 1143.64
#REF! | 22.6527 | 40.4508 | 1143.35
#REF! | 22.6505 | 40.4561 | 1143.27
#REF! | 22.6484 | 40.4614 | 1143.18
#REF! | 22.6462 | 40.4665 | 1143.07
#REF! | 22.644 | 40.4716 | 1142.96
#REF! | 22.6418 | 40.4765 | 1142.85
#REF! | 22.6396 | 40.4813 | 1142.73
#REF! | 22.6374 | 40.486 | 1142.61
#REF! | 22.6352 | 40.4907 | 1142.48
#REF! | 22.633 | 40.4952 | 1142.36
#REF! | 22.6308 | 40.4997 | 1142.23
#REF! | 22.6286 | 40.5041 | 1142.1
#REF! | 22.6264 | 40.5085 | 1141.97
#REF! | 22.6245 | 40.513 | 1141.45
#REF! | 22.6227 | 40.518 | 1140.96
#REF! | 22.621 | 40.5235 | 1140.52
#REF! | 22.6194 | 40.5294 | 1140.09
#REF! | 22.6177 | 40.5358 | 1139.69
#REF! | 22.6162 | 40.5426 | 1139.3
#REF! | 22.6146 | 40.5497 | 1138.93
#REF! | 22.6131 | 40.5571 | 1138.57
#REF! | 22.6115 | 40.5647 | 1138.22
#REF! | 22.6101 | 40.5725 | 1137.89
#REF! | 22.6086 | 40.5805 | 1137.56
#REF! | 22.6071 | 40.5887 | 1137.24
#REF! | 22.6056 | 40.5967 | 1137.14
#REF! | 22.604 | 40.6043 | 1137.05
#REF! | 22.6024 | 40.6117 | 1136.97
#REF! | 22.6007 | 40.6187 | 1136.89
#REF! | 22.599 | 40.6254 | 1136.82
#REF! | 22.5974 | 40.6317 | 1136.75
#REF! | 22.5956 | 40.6377 | 1136.7
#REF! | 22.5939 | 40.6434 | 1136.65
#REF! | 22.5922 | 40.6487 | 1136.62
#REF! | 22.5904 | 40.6536 | 1136.59
#REF! | 22.5886 | 40.6582 | 1136.58
#REF! | 22.5868 | 40.6625 | 1136.57
#REF! | 22.5852 | 40.6668 | 1136.13
#REF! | 22.5838 | 40.6713 | 1135.74
#REF! | 22.5824 | 40.6762 | 1135.39
#REF! | 22.5811 | 40.6813 | 1135.08
#REF! | 22.5798 | 40.6866 | 1134.79
#REF! | 22.5785 | 40.6921 | 1134.53
#REF! | 22.5771 | 40.6977 | 1134.29
#REF! | 22.5758 | 40.7033 | 1134.08
#REF! | 22.5745 | 40.709 | 1133.88
#REF! | 22.5732 | 40.7146 | 1133.7
#REF! | 22.5719 | 40.7202 | 1133.54
#REF! | 22.5706 | 40.7256 | 1133.4
#REF! | 22.5687 | 40.7302 | 1134.15
#REF! | 22.5666 | 40.7334 | 1134.82
#REF! | 22.5642 | 40.7352 | 1135.45
#REF! | 22.5618 | 40.7355 | 1136.05
#REF! | 22.5594 | 40.7344 | 1136.63
#REF! | 22.5568 | 40.732 | 1137.19
#REF! | 22.5542 | 40.7284 | 1137.74
#REF! | 22.5516 | 40.7237 | 1138.28
#REF! | 22.549 | 40.7178 | 1138.82
#REF! | 22.5463 | 40.7109 | 1139.35
#REF! | 22.5436 | 40.7031 | 1139.89
#REF! | 22.5408 | 40.6942 | 1140.44
#REF! | 22.7512 | 40.1666 | 1138.87
#REF! | 22.8506 | 39.919 | 1153.93
#REF! | 22.9031 | 39.7897 | 1160.54
#REF! | 22.9327 | 39.7188 | 1163.61
#REF! | 22.9515 | 39.6762 | 1164.99
#REF! | 22.965 | 39.6485 | 1165.6
#REF! | 22.9755 | 39.6293 | 1165.84
#REF! | 22.9845 | 39.6153 | 1165.91
#REF! | 22.9925 | 39.6049 | 1165.9
#REF! | 23 | 39.5969 | 1165.84
#REF! | 23.0069 | 39.591 | 1165.77
#REF! | 23.1909 | 39.9221 | 1165.7
#REF! | 23.2583 | 39.835 | 1202.36
#REF! | 23.2987 | 39.8054 | 1209.82
#REF! | 23.3253 | 39.8016 | 1215
#REF! | 23.3448 | 39.8082 | 1218.89
#REF! | 23.3603 | 39.8177 | 1222.04
#REF! | 23.3736 | 39.8269 | 1224.7
#REF! | 23.3856 | 39.8344 | 1227.03
#REF! | 23.3965 | 39.8397 | 1229.11
#REF! | 23.4068 | 39.8428 | 1231
#REF! | 23.4165 | 39.8437 | 1232.72
#REF! | 23.4257 | 39.8427 | 1234.3
#REF! | 23.4345 | 39.84 | 1235.76
#REF! | 23.3854 | 39.9093 | 1236.3
#REF! | 23.3648 | 39.9166 | 1230.37
#REF! | 23.3573 | 39.8989 | 1226.84
#REF! | 23.3562 | 39.8716 | 1224.51
#REF! | 23.3582 | 39.8423 | 1222.86
#REF! | 23.3618 | 39.814 | 1221.6
#REF! | 23.3681 | 39.805 | 1220.6
#REF! | 23.374 | 39.7981 | 1220.57
#REF! | 23.3797 | 39.7924 | 1220.55
#REF! | 23.3854 | 39.7876 | 1220.53
#REF! | 23.3912 | 39.7832 | 1220.54
#REF! | 23.397 | 39.7793 | 1220.57
#REF! | 23.4033 | 39.7767 | 1220.02
#REF! | 23.4097 | 39.7754 | 1219.56
#REF! | 23.4164 | 39.7752 | 1219.17
#REF! | 23.4231 | 39.7762 | 1218.83
#REF! | 23.4298 | 39.7783 | 1218.53
#REF! | 23.4367 | 39.7812 | 1218.27
#REF! | 23.4414 | 39.7666 | 1218.04
#REF! | 23.4472 | 39.753 | 1216.97
#REF! | 23.4535 | 39.7413 | 1216.08
#REF! | 23.4601 | 39.7318 | 1215.33
#REF! | 23.4669 | 39.7242 | 1214.67
#REF! | 23.4738 | 39.7186 | 1214.1
#REF! | 23.4869 | 39.8823 | 1214.82
#REF! | 23.4969 | 40.0287 | 1221.47
#REF! | 23.5055 | 40.1571 | 1227.17
#REF! | 23.5133 | 40.2688 | 1232.13
#REF! | 23.5207 | 40.3652 | 1236.47
#REF! | 23.5277 | 40.4481 | 1240.29
#REF! | 23.5345 | 40.5191 | 1243.67
#REF! | 23.5412 | 40.5796 | 1246.67
#REF! | 23.5478 | 40.631 | 1249.33
#REF! | 23.5543 | 40.6745 | 1251.71
#REF! | 23.5606 | 40.711 | 1253.84
#REF! | 23.5669 | 40.7416 | 1255.75
#REF! | 23.3567 | 41.3015 | 1257.87
#REF! | 23.2617 | 41.5674 | 1243.07
#REF! | 23.2155 | 41.7043 | 1236.82
#REF! | 23.1927 | 41.7781 | 1234.14
#REF! | 23.1805 | 41.8217 | 1233.12
#REF! | 23.1735 | 41.8497 | 1232.82
#REF! | 23.1691 | 41.8689 | 1232.84
#REF! | 23.1663 | 41.8823 | 1233.01
#REF! | 23.1644 | 41.8919 | 1233.25
#REF! | 23.1631 | 41.8987 | 1233.51
#REF! | 23.1623 | 41.9031 | 1233.78
#REF! | 23.1619 | 41.9057 | 1234.06
#REF! | 23.3766 | 41.4061 | 1234.14
#REF! | 23.4783 | 41.1947 | 1252.02
#REF! | 23.5321 | 41.1006 | 1261.2
#REF! | 23.5627 | 41.0606 | 1266.62
#REF! | 23.5825 | 41.0437 | 1270.15
#REF! | 23.5968 | 41.0365 | 1272.72
#REF! | 23.6083 | 41.0328 | 1274.78
#REF! | 23.6182 | 41.0301 | 1276.52
#REF! | 23.6272 | 41.0271 | 1278.04
#REF! | 23.6355 | 41.0231 | 1279.42
#REF! | 23.6434 | 41.0183 | 1280.68
#REF! | 23.6508 | 41.0126 | 1281.84
#REF! | 23.6578 | 41.0057 | 1283.15
#REF! | 23.6645 | 40.9978 | 1284.37
#REF! | 23.6709 | 40.9891 | 1285.51
#REF! | 23.677 | 40.9793 | 1286.58
#REF! | 23.6829 | 40.9688 | 1287.6
#REF! | 23.6886 | 40.9577 | 1288.57
#REF! | 23.7703 | 41.4711 | 1289.49
#REF! | 23.8163 | 41.9806 | 1317.78
#REF! | 23.8458 | 42.4504 | 1340.66
#REF! | 23.8669 | 42.8707 | 1359.9
#REF! | 23.8835 | 43.2405 | 1376.38
#REF! | 23.8977 | 43.5629 | 1390.69
#REF! | 23.9111 | 43.843 | 1401.91
#REF! | 23.9237 | 44.0866 | 1411.76
#REF! | 23.9356 | 44.2984 | 1420.4
#REF! | 23.947 | 44.4824 | 1427.98
#REF! | 23.9577 | 44.6426 | 1434.64
#REF! | 23.968 | 44.7818 | 1440.49
#REF! | 23.9778 | 44.9029 | 1445.63
#REF! | 23.9871 | 45.0083 | 1450.16
#REF! | 23.996 | 45.1 | 1454.15
#REF! | 24.0045 | 45.1797 | 1457.66
#REF! | 24.0127 | 45.2493 | 1460.76
#REF! | 24.0205 | 45.3099 | 1463.5
#REF! | 24.0273 | 45.3622 | 1467.05
#REF! | 24.0335 | 45.4067 | 1470.18
#REF! | 24.0391 | 45.4441 | 1472.97
#REF! | 24.0442 | 45.4752 | 1475.45
#REF! | 24.049 | 45.5008 | 1477.67
#REF! | 24.0536 | 45.5215 | 1479.67
#REF! | 24.0578 | 45.538 | 1481.47
#REF! | 24.0618 | 45.5508 | 1483.1
#REF! | 24.0656 | 45.5606 | 1484.58
#REF! | 24.0691 | 45.5676 | 1485.92
#REF! | 24.0724 | 45.5724 | 1487.14
#REF! | 24.0754 | 45.5754 | 1488.26
#REF! | 24.1497 | 46.3839 | 1489.28
#REF! | 24.1895 | 47.136 | 1527.73
#REF! | 24.2132 | 47.8024 | 1559.53
#REF! | 24.2287 | 48.3806 | 1585.89
#REF! | 24.2398 | 48.876 | 1608.02
#REF! | 24.2484 | 49.2975 | 1626.71
#REF! | 23.9893 | 49.9171 | 1633.91
#REF! | 23.7692 | 50.3289 | 1612.08
#REF! | 23.6954 | 50.3634 | 1595.01
#REF! | 23.6568 | 50.3091 | 1583.96
#REF! | 23.6339 | 50.2256 | 1576.09
#REF! | 23.6183 | 50.1371 | 1569.97
#REF! | 23.6064 | 50.0531 | 1564.95
#REF! | 23.5966 | 49.9768 | 1560.71
#REF! | 23.588 | 49.909 | 1557.06
#REF! | 23.5801 | 49.8498 | 1553.9
#REF! | 23.5728 | 49.798 | 1551.13
#REF! | 23.566 | 49.7532 | 1548.71
#REF! | 23.4531 | 50.0345 | 1546.58
#REF! | 23.3995 | 50.1357 | 1536.86
#REF! | 23.3698 | 50.1674 | 1531.44
#REF! | 23.3512 | 50.1698 | 1527.87
#REF! | 23.3376 | 50.1616 | 1525.26
#REF! | 23.3265 | 50.1506 | 1523.16
#REF! | 23.3738 | 50.3131 | 1521.57
#REF! | 23.3923 | 50.525 | 1535.3
#REF! | 23.399 | 50.7373 | 1545.73
#REF! | 23.4002 | 50.9346 | 1554.18
#REF! | 23.399 | 51.1112 | 1561.22
#REF! | 23.3967 | 51.2668 | 1567.21
#REF! | 23.3938 | 51.4029 | 1572.34
#REF! | 23.3905 | 51.5214 | 1576.76
#REF! | 23.3871 | 51.6244 | 1580.57
#REF! | 23.3835 | 51.7139 | 1583.85
#REF! | 23.3798 | 51.7916 | 1586.68
#REF! | 23.3761 | 51.8589 | 1589.13
#REF! | 23.2987 | 50.4038 | 1590.33
#REF! | 23.2496 | 49.0759 | 1531.23
#REF! | 23.2157 | 47.8921 | 1481.22
#REF! | 23.1899 | 46.8514 | 1438.44
#REF! | 23.1684 | 45.9436 | 1401.63
#REF! | 23.1488 | 45.1544 | 1371.1
#REF! | 23.1307 | 44.469 | 1344.42
#REF! | 23.114 | 43.8742 | 1321.09
#REF! | 23.0985 | 43.3586 | 1300.69
#REF! | 23.084 | 42.9121 | 1282.82
#REF! | 23.0705 | 42.5258 | 1267.17
#REF! | 23.0578 | 42.192 | 1253.45
#REF! | 23.0449 | 41.903 | 1242.85
#REF! | 23.0322 | 41.6519 | 1233.53
#REF! | 23.0199 | 41.4336 | 1225.36
#REF! | 23.0081 | 41.2436 | 1218.22
#REF! | 22.9966 | 41.0781 | 1211.96
#REF! | 22.9855 | 40.934 | 1206.47
#REF! | 22.9748 | 40.8086 | 1201.68
#REF! | 22.9645 | 40.6993 | 1197.47
#REF! | 22.9544 | 40.604 | 1193.78
#REF! | 22.9446 | 40.521 | 1190.55
#REF! | 22.9351 | 40.4486 | 1187.71
#REF! | 22.9259 | 40.3855 | 1185.22
#REF! | 22.9173 | 40.3311 | 1182.3
#REF! | 22.9092 | 40.2845 | 1179.73
#REF! | 22.9014 | 40.2451 | 1177.45
#REF! | 22.8939 | 40.212 | 1175.43
#REF! | 22.8865 | 40.1842 | 1173.63
#REF! | 22.8794 | 40.1612 | 1172.02
#REF! | 22.8724 | 40.1423 | 1170.58
#REF! | 22.8656 | 40.127 | 1169.28
#REF! | 22.859 | 40.1147 | 1168.11
#REF! | 22.8525 | 40.105 | 1167.06
#REF! | 22.8461 | 40.0977 | 1166.1
#REF! | 22.8399 | 40.0923 | 1165.23
#REF! | 22.8335 | 40.0882 | 1164.85
#REF! | 22.8271 | 40.085 | 1164.49
#REF! | 22.8208 | 40.0824 | 1164.15
#REF! | 22.8145 | 40.0804 | 1163.84
#REF! | 22.8084 | 40.0785 | 1163.54
#REF! | 22.8022 | 40.0772 | 1163.28
#REF! | 22.7962 | 40.076 | 1163.03
#REF! | 22.7903 | 40.0749 | 1162.8
#REF! | 22.7845 | 40.0741 | 1162.59
#REF! | 22.7787 | 40.0734 | 1162.39
#REF! | 22.773 | 40.0728 | 1162.21
#REF! | 22.7674 | 40.0724 | 1162.03
#REF! | 22.7622 | 40.0725 | 1161.17
#REF! | 22.7573 | 40.0737 | 1160.4
#REF! | 22.7526 | 40.0758 | 1159.7
#REF! | 22.7481 | 40.0788 | 1159.05
#REF! | 22.7436 | 40.0827 | 1158.45
#REF! | 22.7392 | 40.0873 | 1157.89
#REF! | 22.7349 | 40.0926 | 1157.36
#REF! | 22.7307 | 40.0984 | 1156.86
#REF! | 22.7265 | 40.1046 | 1156.39
#REF! | 22.7224 | 40.1112 | 1155.94
#REF! | 22.7183 | 40.1181 | 1155.51
#REF! | 22.7143 | 40.1253 | 1155.1
#REF! | 22.7102 | 40.1324 | 1155.03
#REF! | 22.706 | 40.1393 | 1154.93
#REF! | 22.7018 | 40.1459 | 1154.82
#REF! | 22.6976 | 40.1521 | 1154.7
#REF! | 22.6935 | 40.1581 | 1154.57
#REF! | 22.6894 | 40.1638 | 1154.45
#REF! | 22.6853 | 40.1692 | 1154.31
#REF! | 22.6812 | 40.1744 | 1154.18
#REF! | 22.6772 | 40.1793 | 1154.04
#REF! | 22.6732 | 40.1841 | 1153.9
#REF! | 22.6693 | 40.1887 | 1153.76
#REF! | 22.6654 | 40.1931 | 1153.62
#REF! | 22.6619 | 40.1979 | 1152.78
#REF! | 22.6587 | 40.2035 | 1152.03
#REF! | 22.6557 | 40.21 | 1151.34
#REF! | 22.6527 | 40.2173 | 1150.69
#REF! | 22.6499 | 40.2252 | 1150.09
#REF! | 22.647 | 40.2339 | 1149.52
#REF! | 22.6443 | 40.243 | 1148.97
#REF! | 22.6415 | 40.2527 | 1148.46
#REF! | 22.6389 | 40.2627 | 1147.96
#REF! | 22.6362 | 40.273 | 1147.48
#REF! | 22.6337 | 40.2837 | 1147.03
#REF! | 22.6311 | 40.2945 | 1146.58
#REF! | 22.6286 | 40.3054 | 1146.26
#REF! | 22.626 | 40.3163 | 1145.93
#REF! | 22.6235 | 40.3271 | 1145.6
#REF! | 22.621 | 40.3378 | 1145.28
#REF! | 22.6186 | 40.3485 | 1144.96
#REF! | 22.6162 | 40.3591 | 1144.64
#REF! | 22.6138 | 40.3696 | 1144.33
#REF! | 22.6114 | 40.3801 | 1144.02
#REF! | 22.6091 | 40.3904 | 1143.71
#REF! | 22.6068 | 40.4008 | 1143.4
#REF! | 22.6045 | 40.411 | 1143.1
#REF! | 22.6023 | 40.4212 | 1142.8
#REF! | 22.6005 | 40.4316 | 1141.93
#REF! | 22.5988 | 40.4426 | 1141.14
#REF! | 22.5974 | 40.4543 | 1140.4
#REF! | 22.5959 | 40.4667 | 1139.71
#REF! | 22.5946 | 40.4796 | 1139.06
#REF! | 22.5933 | 40.4929 | 1138.44
#REF! | 22.592 | 40.5068 | 1137.85
#REF! | 22.5908 | 40.5209 | 1137.29
#REF! | 22.5896 | 40.5353 | 1136.75
#REF! | 22.5884 | 40.5498 | 1136.23
#REF! | 22.5872 | 40.5646 | 1135.74
#REF! | 22.5861 | 40.5794 | 1135.26
#REF! | 22.5851 | 40.5946 | 1134.49
#REF! | 22.5843 | 40.6102 | 1133.77
#REF! | 22.5836 | 40.6263 | 1133.08
#REF! | 22.5829 | 40.6427 | 1132.42
#REF! | 22.5823 | 40.6595 | 1131.79
#REF! | 22.5817 | 40.6766 | 1131.17
#REF! | 22.5811 | 40.6939 | 1130.57
#REF! | 22.5806 | 40.7114 | 1129.99
#REF! | 22.5801 | 40.729 | 1129.42
#REF! | 22.5797 | 40.7468 | 1128.87
#REF! | 22.5793 | 40.7646 | 1128.33
#REF! | 22.5789 | 40.7824 | 1127.8
#REF! | 22.578 | 40.7995 | 1128.14
#REF! | 22.5769 | 40.8155 | 1128.39
#REF! | 22.5757 | 40.8301 | 1128.6
#REF! | 22.5744 | 40.8436 | 1128.78
#REF! | 22.5731 | 40.8558 | 1128.92
#REF! | 22.5718 | 40.8669 | 1129.05
#REF! | 22.5705 | 40.8769 | 1129.16
#REF! | 22.5692 | 40.886 | 1129.27
#REF! | 22.5679 | 40.8942 | 1129.36
#REF! | 22.5666 | 40.9016 | 1129.45
#REF! | 22.5653 | 40.9081 | 1129.54
#REF! | 22.5641 | 40.9139 | 1129.63
#REF! | 22.7751 | 40.3972 | 1128.93
#REF! | 22.8752 | 40.1595 | 1144.67
#REF! | 22.928 | 40.0391 | 1151.92
#REF! | 22.9579 | 39.9758 | 1155.57
#REF! | 22.9767 | 39.9397 | 1157.48
#REF! | 22.9901 | 39.9173 | 1158.55
#REF! | 23.0006 | 39.9023 | 1159.23
#REF! | 23.0094 | 39.8915 | 1159.69
#REF! | 23.0172 | 39.8833 | 1160.03
#REF! | 23.0244 | 39.8767 | 1160.31
#REF! | 23.0312 | 39.8714 | 1160.55
#REF! | 23.2145 | 40.2005 | 1160.77
#REF! | 23.2832 | 40.1133 | 1195.55
#REF! | 23.3257 | 40.0863 | 1201.38
#REF! | 23.3547 | 40.0879 | 1205.07
#REF! | 23.3767 | 40.1024 | 1207.59
#REF! | 23.395 | 40.1221 | 1209.45
#REF! | 23.4112 | 40.1436 | 1210.9
#REF! | 23.4261 | 40.1651 | 1212.08
#REF! | 23.4402 | 40.1862 | 1213.07
#REF! | 23.4536 | 40.2064 | 1213.9
#REF! | 23.4665 | 40.2257 | 1214.6
#REF! | 23.4791 | 40.2443 | 1215.21
#REF! | 23.4914 | 40.2621 | 1215.72
#REF! | 23.4442 | 40.3514 | 1218.1
#REF! | 23.4243 | 40.3763 | 1213.75
#REF! | 23.4172 | 40.3726 | 1211.56
#REF! | 23.4162 | 40.3562 | 1210.42
#REF! | 23.4183 | 40.3348 | 1209.84
#REF! | 23.4218 | 40.3119 | 1209.57
#REF! | 23.4277 | 40.3126 | 1209.46
#REF! | 23.4334 | 40.3122 | 1210.43
#REF! | 23.4389 | 40.3103 | 1211.31
#REF! | 23.4444 | 40.3071 | 1212.14
#REF! | 23.4498 | 40.3024 | 1212.92
#REF! | 23.4553 | 40.2966 | 1213.67
#REF! | 23.4608 | 40.2896 | 1214.36
#REF! | 23.4664 | 40.2817 | 1215.02
#REF! | 23.4719 | 40.273 | 1215.66
#REF! | 23.4775 | 40.2636 | 1216.29
#REF! | 23.4831 | 40.2537 | 1216.9
#REF! | 23.4888 | 40.2431 | 1217.49
#REF! | 23.4925 | 40.2094 | 1218.08
#REF! | 23.4972 | 40.1766 | 1217.7
#REF! | 23.5022 | 40.1456 | 1217.48
#REF! | 23.5075 | 40.1165 | 1217.38
#REF! | 23.5129 | 40.0891 | 1217.37
#REF! | 23.5185 | 40.0633 | 1217.43
#REF! | 23.5309 | 40.2072 | 1217.63
#REF! | 23.5406 | 40.3351 | 1223.9
#REF! | 23.5491 | 40.4463 | 1229.3
#REF! | 23.5569 | 40.5422 | 1234.02
#REF! | 23.5643 | 40.624 | 1238.18
#REF! | 23.5714 | 40.6933 | 1241.87
#REF! | 23.5784 | 40.7517 | 1245.15
#REF! | 23.5853 | 40.8005 | 1248.09
#REF! | 23.5921 | 40.841 | 1250.73
#REF! | 23.5989 | 40.8741 | 1253.1
#REF! | 23.6055 | 40.9008 | 1255.25
#REF! | 23.6121 | 40.922 | 1257.19
#REF! | 23.4035 | 41.4759 | 1257.62
#REF! | 23.3104 | 41.7375 | 1241.42
#REF! | 23.2665 | 41.8724 | 1233.89
#REF! | 23.2461 | 41.9465 | 1230.05
#REF! | 23.2365 | 41.9924 | 1227.97
#REF! | 23.2321 | 42.0247 | 1226.71
#REF! | 23.2305 | 42.0499 | 1225.85
#REF! | 23.2304 | 42.0709 | 1225.21
#REF! | 23.2313 | 42.0893 | 1224.69
#REF! | 23.2329 | 42.1061 | 1224.26
#REF! | 23.235 | 42.1215 | 1223.88
#REF! | 23.2375 | 42.1357 | 1223.55
#REF! | 23.4543 | 41.6449 | 1224.48
#REF! | 23.5579 | 41.4417 | 1242.98
#REF! | 23.6135 | 41.355 | 1252.76
#REF! | 23.6456 | 41.3216 | 1258.73
#REF! | 23.6667 | 41.3103 | 1262.75
#REF! | 23.6823 | 41.3077 | 1265.77
#REF! | 23.695 | 41.3077 | 1268.22
#REF! | 23.7061 | 41.3078 | 1270.33
#REF! | 23.7161 | 41.3069 | 1272.19
#REF! | 23.7256 | 41.3043 | 1273.87
#REF! | 23.7345 | 41.3004 | 1275.41
#REF! | 23.7429 | 41.2949 | 1276.83
#REF! | 23.7514 | 41.2884 | 1277.74
#REF! | 23.7596 | 41.2813 | 1278.62
#REF! | 23.7677 | 41.2737 | 1279.47
#REF! | 23.7755 | 41.2656 | 1280.29
#REF! | 23.7831 | 41.2573 | 1281.09
#REF! | 23.7905 | 41.2488 | 1281.85
#REF! | 23.8733 | 41.7637 | 1282.6
#REF! | 23.9207 | 42.2748 | 1310.75
#REF! | 23.9517 | 42.7465 | 1333.54
#REF! | 23.9737 | 43.1687 | 1353.7
#REF! | 23.991 | 43.5398 | 1370.95
#REF! | 24.0056 | 43.8628 | 1385.85
#REF! | 24.019 | 44.1423 | 1398.33
#REF! | 24.0313 | 44.3839 | 1409.23
#REF! | 24.0429 | 44.5923 | 1418.75
#REF! | 24.0539 | 44.7718 | 1427.08
#REF! | 24.0642 | 44.9264 | 1434.38
#REF! | 24.0741 | 45.0594 | 1440.79
#REF! | 24.0835 | 45.1735 | 1446.43
#REF! | 24.0924 | 45.2715 | 1451.39
#REF! | 24.1009 | 45.3555 | 1455.76
#REF! | 24.1091 | 45.4274 | 1459.61
#REF! | 24.1169 | 45.4889 | 1463.03
#REF! | 24.1243 | 45.5414 | 1466.05
#REF! | 24.1308 | 45.5855 | 1469.88
#REF! | 24.1364 | 45.6218 | 1473.27
#REF! | 24.1416 | 45.6509 | 1476.28
#REF! | 24.1465 | 45.6735 | 1478.99
#REF! | 24.1509 | 45.691 | 1481.41
#REF! | 24.1549 | 45.7037 | 1483.6
#REF! | 24.1587 | 45.7122 | 1485.57
#REF! | 24.1622 | 45.7173 | 1487.36
#REF! | 24.1655 | 45.7193 | 1489
#REF! | 24.1685 | 45.7188 | 1490.48
#REF! | 24.1713 | 45.7162 | 1491.85
#REF! | 24.1738 | 45.7119 | 1493.1
#REF! | 24.224 | 46.7112 | 1494.69
#REF! | 24.2519 | 47.5916 | 1537.09
#REF! | 24.2693 | 48.3481 | 1572.04
#REF! | 24.281 | 48.9899 | 1601.2
#REF! | 24.2895 | 49.5299 | 1625.67
#REF! | 24.296 | 49.9809 | 1646.25
#REF! | 24.0535 | 50.4989 | 1654.71
#REF! | 23.8471 | 50.7866 | 1632.96
#REF! | 23.7767 | 50.7499 | 1615.15
#REF! | 23.739 | 50.6377 | 1603.18
#REF! | 23.7158 | 50.5049 | 1594.41
#REF! | 23.6993 | 50.3733 | 1587.47
#REF! | 23.6866 | 50.2509 | 1581.36
#REF! | 23.6759 | 50.1406 | 1576.18
#REF! | 23.6664 | 50.0426 | 1571.73
#REF! | 23.6576 | 49.9564 | 1567.87
#REF! | 23.6494 | 49.8805 | 1564.52
#REF! | 23.6417 | 49.814 | 1561.59
#REF! | 23.528 | 50.0755 | 1559.03
#REF! | 23.4735 | 50.1587 | 1548.96
#REF! | 23.4429 | 50.174 | 1543.25
#REF! | 23.4234 | 50.1617 | 1539.43
#REF! | 23.4089 | 50.1401 | 1536.6
#REF! | 23.3967 | 50.1168 | 1534.32
#REF! | 23.443 | 50.2698 | 1532.05
#REF! | 23.4608 | 50.4727 | 1545.19
#REF! | 23.4669 | 50.6774 | 1555.11
#REF! | 23.4677 | 50.8682 | 1563.12
#REF! | 23.4661 | 51.0396 | 1569.78
#REF! | 23.4634 | 51.191 | 1575.42
#REF! | 23.4601 | 51.3238 | 1580.24
#REF! | 23.4565 | 51.4399 | 1584.38
#REF! | 23.4527 | 51.5412 | 1587.94
#REF! | 23.4487 | 51.6296 | 1590.99
#REF! | 23.4447 | 51.7066 | 1593.62
#REF! | 23.4406 | 51.7739 | 1595.86
#REF! | 23.3636 | 50.3149 | 1597.96
#REF! | 23.3139 | 48.9842 | 1539.62
#REF! | 23.2788 | 47.7973 | 1490.22
#REF! | 23.2516 | 46.7527 | 1447.94
#REF! | 23.2287 | 45.8399 | 1411.5
#REF! | 23.2084 | 45.0454 | 1379.94
#REF! | 23.1894 | 44.3551 | 1353.44
#REF! | 23.1712 | 43.755 | 1330.9
#REF! | 23.1539 | 43.2331 | 1311.19
#REF! | 23.1375 | 42.7793 | 1293.97
#REF! | 23.1219 | 42.3848 | 1278.9
#REF! | 23.1071 | 42.0419 | 1265.72
#REF! | 23.0931 | 41.7441 | 1254
#REF! | 23.0798 | 41.4857 | 1243.74
#REF! | 23.0672 | 41.2616 | 1234.75
#REF! | 23.055 | 41.0676 | 1226.86
#REF! | 23.0434 | 40.8997 | 1219.94
#REF! | 23.0322 | 40.7546 | 1213.85
#REF! | 23.0213 | 40.6292 | 1208.5
#REF! | 23.0109 | 40.5211 | 1203.79
#REF! | 23.0008 | 40.428 | 1199.63
#REF! | 22.991 | 40.3479 | 1195.96
#REF! | 22.9815 | 40.2791 | 1192.72
#REF! | 22.9722 | 40.2202 | 1189.85
#REF! | 22.9636 | 40.1702 | 1186.78
#REF! | 22.9553 | 40.1284 | 1184.05
#REF! | 22.9473 | 40.0937 | 1181.62
#REF! | 22.9396 | 40.0653 | 1179.44
#REF! | 22.9321 | 40.0424 | 1177.48
#REF! | 22.9248 | 40.0243 | 1175.71
#REF! | 22.9177 | 40.0103 | 1174.11
#REF! | 22.9107 | 39.9998 | 1172.65
#REF! | 22.9039 | 39.9924 | 1171.33
#REF! | 22.8973 | 39.9878 | 1170.12
#REF! | 22.8908 | 39.9853 | 1169
#REF! | 22.8844 | 39.9849 | 1167.98
#REF! | 22.8781 | 39.9861 | 1167.16
#REF! | 22.8718 | 39.9885 | 1166.4
#REF! | 22.8657 | 39.992 | 1165.68
#REF! | 22.8596 | 39.9965 | 1165.01
#REF! | 22.8537 | 40.0016 | 1164.38
#REF! | 22.8478 | 40.0074 | 1163.79
#REF! | 22.842 | 40.0137 | 1163.22
#REF! | 22.8363 | 40.0205 | 1162.69
#REF! | 22.8307 | 40.0276 | 1162.18
#REF! | 22.8251 | 40.0351 | 1161.7
#REF! | 22.8197 | 40.0427 | 1161.24
#REF! | 22.8143 | 40.0506 | 1160.79
#REF! | 22.8089 | 40.0581 | 1160.68
#REF! | 22.8034 | 40.0652 | 1160.55
#REF! | 22.798 | 40.072 | 1160.4
#REF! | 22.7926 | 40.0786 | 1160.25
#REF! | 22.7872 | 40.0848 | 1160.09
#REF! | 22.7819 | 40.0906 | 1159.93
#REF! | 22.7766 | 40.0963 | 1159.76
#REF! | 22.7713 | 40.1016 | 1159.59
#REF! | 22.7661 | 40.1067 | 1159.42
#REF! | 22.7609 | 40.1116 | 1159.24
#REF! | 22.7558 | 40.1163 | 1159.07
#REF! | 22.7507 | 40.1208 | 1158.9
#REF! | 22.7459 | 40.1255 | 1158.35
#REF! | 22.7413 | 40.1305 | 1157.84
#REF! | 22.7367 | 40.1359 | 1157.37
#REF! | 22.7323 | 40.1416 | 1156.93
#REF! | 22.7279 | 40.1477 | 1156.5
#REF! | 22.7235 | 40.1541 | 1156.1
#REF! | 22.7192 | 40.1607 | 1155.71
#REF! | 22.715 | 40.1674 | 1155.33
#REF! | 22.7108 | 40.1744 | 1154.97
#REF! | 22.7066 | 40.1815 | 1154.62
#REF! | 22.7025 | 40.1886 | 1154.28
#REF! | 22.6985 | 40.1959 | 1153.95
#REF! | 22.6944 | 40.2032 | 1153.63
#REF! | 22.6905 | 40.2105 | 1153.32
#REF! | 22.6865 | 40.2178 | 1153.01
#REF! | 22.6826 | 40.2252 | 1152.71
#REF! | 22.6788 | 40.2325 | 1152.42
#REF! | 22.675 | 40.2399 | 1152.13
#REF! | 22.6712 | 40.2472 | 1151.85
#REF! | 22.6674 | 40.2545 | 1151.57
#REF! | 22.6637 | 40.2617 | 1151.3
#REF! | 22.66 | 40.2689 | 1151.03
#REF! | 22.6564 | 40.2761 | 1150.77
#REF! | 22.6528 | 40.2832 | 1150.51
#REF! | 22.6497 | 40.2908 | 1149.61
#REF! | 22.6468 | 40.299 | 1148.78
#REF! | 22.644 | 40.3082 | 1148.01
#REF! | 22.6414 | 40.3181 | 1147.29
#REF! | 22.6388 | 40.3287 | 1146.6
#REF! | 22.6363 | 40.34 | 1145.95
#REF! | 22.6339 | 40.3518 | 1145.32
#REF! | 22.6315 | 40.3641 | 1144.71
#REF! | 22.6292 | 40.3768 | 1144.12
#REF! | 22.6269 | 40.3898 | 1143.55
#REF! | 22.6247 | 40.4031 | 1143
#REF! | 22.6225 | 40.4167 | 1142.46
#REF! | 22.6212 | 40.4314 | 1140.7
#REF! | 22.6203 | 40.4478 | 1139.08
#REF! | 22.6197 | 40.466 | 1137.57
#REF! | 22.6193 | 40.4861 | 1136.15
#REF! | 22.619 | 40.5077 | 1134.79
#REF! | 22.6189 | 40.5308 | 1133.5
#REF! | 22.6188 | 40.5551 | 1132.25
#REF! | 22.6188 | 40.5806 | 1131.05
#REF! | 22.6189 | 40.607 | 1129.89
#REF! | 22.6191 | 40.6342 | 1128.76
#REF! | 22.6194 | 40.6622 | 1127.66
#REF! | 22.6197 | 40.6908 | 1126.58
#REF! | 22.6196 | 40.7194 | 1126.24
#REF! | 22.6194 | 40.7475 | 1125.85
#REF! | 22.6192 | 40.775 | 1125.43
#REF! | 22.6189 | 40.8019 | 1124.98
#REF! | 22.6186 | 40.8281 | 1124.53
#REF! | 22.6183 | 40.8538 | 1124.05
#REF! | 22.618 | 40.8789 | 1123.58
#REF! | 22.6178 | 40.9035 | 1123.09
#REF! | 22.6176 | 40.9277 | 1122.6
#REF! | 22.6174 | 40.9514 | 1122.11
#REF! | 22.6173 | 40.9748 | 1121.62
#REF! | 22.6172 | 40.9977 | 1121.12
#REF! | 22.616 | 41.0191 | 1122.24
#REF! | 22.6144 | 41.0379 | 1123.2
#REF! | 22.6126 | 41.054 | 1124.06
#REF! | 22.6106 | 41.0676 | 1124.84
#REF! | 22.6084 | 41.0787 | 1125.55
#REF! | 22.6062 | 41.0876 | 1126.23
#REF! | 22.604 | 41.0944 | 1126.86
#REF! | 22.6017 | 41.0993 | 1127.47
#REF! | 22.5994 | 41.1025 | 1128.05
#REF! | 22.597 | 41.104 | 1128.62
#REF! | 22.5946 | 41.104 | 1129.18
#REF! | 22.5921 | 41.1026 | 1129.73
#REF! | 22.8028 | 40.5768 | 1128.23
#REF! | 22.9029 | 40.3321 | 1143.27
#REF! | 22.9561 | 40.2066 | 1149.92
#REF! | 22.9862 | 40.1398 | 1153.03
#REF! | 23.0055 | 40.1015 | 1154.45
#REF! | 23.0193 | 40.0781 | 1155.07
#REF! | 23.0302 | 40.063 | 1155.33
#REF! | 23.0396 | 40.053 | 1155.4
#REF! | 23.0479 | 40.0462 | 1155.38
#REF! | 23.0557 | 40.0418 | 1155.32
#REF! | 23.0631 | 40.0392 | 1155.24
#REF! | 23.2467 | 40.3706 | 1155.14
#REF! | 23.3153 | 40.2859 | 1190.94
#REF! | 23.3573 | 40.2604 | 1197.68
#REF! | 23.3856 | 40.2621 | 1202.19
#REF! | 23.4067 | 40.2753 | 1205.47
#REF! | 23.4239 | 40.2926 | 1208.02
#REF! | 23.439 | 40.3103 | 1210.12
#REF! | 23.4528 | 40.327 | 1211.92
#REF! | 23.4656 | 40.3422 | 1213.49
#REF! | 23.4778 | 40.3556 | 1214.87
#REF! | 23.4895 | 40.3674 | 1216.11
#REF! | 23.5008 | 40.3776 | 1217.22
#REF! | 23.5117 | 40.3865 | 1218.23
#REF! | 23.464 | 40.4671 | 1219.91
#REF! | 23.444 | 40.4841 | 1214.96
#REF! | 23.4368 | 40.4737 | 1212.27
#REF! | 23.436 | 40.4516 | 1210.68
#REF! | 23.4383 | 40.4255 | 1209.71
#REF! | 23.4421 | 40.3989 | 1209.08
#REF! | 23.4488 | 40.3964 | 1208.66
#REF! | 23.4549 | 40.3939 | 1209.39
#REF! | 23.461 | 40.3908 | 1210.06
#REF! | 23.4669 | 40.387 | 1210.68
#REF! | 23.4729 | 40.3822 | 1211.28
#REF! | 23.4789 | 40.3767 | 1211.85
#REF! | 23.4849 | 40.3703 | 1212.32
#REF! | 23.4911 | 40.3635 | 1212.79
#REF! | 23.4973 | 40.3562 | 1213.25
#REF! | 23.5035 | 40.3485 | 1213.7
#REF! | 23.5098 | 40.3405 | 1214.15
#REF! | 23.5162 | 40.3321 | 1214.6
#REF! | 23.5202 | 40.3006 | 1215.05
#REF! | 23.5254 | 40.2698 | 1214.47
#REF! | 23.5312 | 40.2407 | 1214.08
#REF! | 23.5372 | 40.2135 | 1213.83
#REF! | 23.5434 | 40.1883 | 1213.67
#REF! | 23.5498 | 40.1647 | 1213.6
#REF! | 23.5633 | 40.3111 | 1213.16
#REF! | 23.5745 | 40.4421 | 1218.85
#REF! | 23.5845 | 40.5573 | 1223.72
#REF! | 23.5938 | 40.6578 | 1227.96
#REF! | 23.6029 | 40.7449 | 1231.68
#REF! | 23.6118 | 40.8201 | 1234.95
#REF! | 23.6205 | 40.8849 | 1237.84
#REF! | 23.6292 | 40.9405 | 1240.4
#REF! | 23.6378 | 40.9882 | 1242.69
#REF! | 23.6464 | 41.0288 | 1244.72
#REF! | 23.655 | 41.0633 | 1246.54
#REF! | 23.6635 | 41.0925 | 1248.18
#REF! | 23.4551 | 41.6556 | 1250.76
#REF! | 23.3613 | 41.9227 | 1236.43
#REF! | 23.3165 | 42.0592 | 1230.54
#REF! | 23.295 | 42.1314 | 1228.18
#REF! | 23.2842 | 42.1725 | 1227.46
#REF! | 23.2787 | 42.1973 | 1227.45
#REF! | 23.2758 | 42.2128 | 1227.76
#REF! | 23.2744 | 42.2222 | 1228.19
#REF! | 23.274 | 42.2274 | 1228.68
#REF! | 23.2742 | 42.2295 | 1229.2
#REF! | 23.275 | 42.2291 | 1229.71
#REF! | 23.2761 | 42.2265 | 1230.23
#REF! | 23.492 | 41.7178 | 1230.98
#REF! | 23.5949 | 41.4981 | 1249.4
#REF! | 23.6499 | 41.396 | 1259.14
#REF! | 23.6816 | 41.3479 | 1265.1
#REF! | 23.7023 | 41.3228 | 1269.14
#REF! | 23.7176 | 41.3068 | 1272.21
#REF! | 23.73 | 41.2941 | 1274.73
#REF! | 23.7408 | 41.2821 | 1276.92
#REF! | 23.7506 | 41.2694 | 1278.88
#REF! | 23.7597 | 41.2555 | 1280.67
#REF! | 23.7683 | 41.2406 | 1282.34
#REF! | 23.7766 | 41.2246 | 1283.9
#REF! | 23.7847 | 41.2077 | 1285.04
#REF! | 23.7926 | 41.1903 | 1286.15
#REF! | 23.8003 | 41.1727 | 1287.22
#REF! | 23.8078 | 41.1546 | 1288.26
#REF! | 23.815 | 41.1365 | 1289.27
#REF! | 23.8221 | 41.1182 | 1290.25
#REF! | 23.9042 | 41.6242 | 1291.2
#REF! | 23.951 | 42.1262 | 1319.56
#REF! | 23.9815 | 42.5888 | 1342.54
#REF! | 24.0037 | 43.0022 | 1361.9
#REF! | 24.0215 | 43.3655 | 1378.52
#REF! | 24.0368 | 43.6817 | 1392.95
#REF! | 24.0514 | 43.9559 | 1404.25
#REF! | 24.0651 | 44.194 | 1414.32
#REF! | 24.0776 | 44.4004 | 1423.74
#REF! | 24.0895 | 44.5786 | 1431.95
#REF! | 24.1006 | 44.7325 | 1439.14
#REF! | 24.1112 | 44.8651 | 1445.44
#REF! | 24.1214 | 44.9793 | 1450.97
#REF! | 24.131 | 45.0776 | 1455.83
#REF! | 24.1403 | 45.1622 | 1460.11
#REF! | 24.1492 | 45.2348 | 1463.87
#REF! | 24.1577 | 45.2973 | 1467.2
#REF! | 24.1659 | 45.3509 | 1470.14
#REF! | 24.1731 | 45.3964 | 1473.73
#REF! | 24.1797 | 45.4343 | 1476.9
#REF! | 24.1857 | 45.4654 | 1479.72
#REF! | 24.1915 | 45.4903 | 1482.25
#REF! | 24.1968 | 45.5102 | 1484.51
#REF! | 24.2017 | 45.5258 | 1486.54
#REF! | 24.2064 | 45.5374 | 1488.37
#REF! | 24.2107 | 45.5458 | 1490.02
#REF! | 24.2148 | 45.5513 | 1491.52
#REF! | 24.2187 | 45.5544 | 1492.89
#REF! | 24.2223 | 45.5555 | 1494.13
#REF! | 24.2256 | 45.5549 | 1495.27
#REF! | 24.2921 | 46.5039 | 1495.77
#REF! | 24.3287 | 47.3682 | 1537.95
#REF! | 24.3517 | 48.1287 | 1572.59
#REF! | 24.3675 | 48.7883 | 1601.59
#REF! | 24.3796 | 49.3556 | 1626.1
#REF! | 24.3894 | 49.8416 | 1646.94
#REF! | 24.137 | 50.3956 | 1655.69
#REF! | 23.9231 | 50.7184 | 1632.19
#REF! | 23.8516 | 50.6974 | 1613.1
#REF! | 23.8144 | 50.5973 | 1600.16
#REF! | 23.7923 | 50.4759 | 1590.57
#REF! | 23.7774 | 50.3557 | 1582.92
#REF! | 23.7658 | 50.245 | 1576.87
#REF! | 23.7561 | 50.146 | 1571.71
#REF! | 23.7476 | 50.0589 | 1567.26
#REF! | 23.7397 | 49.9831 | 1563.38
#REF! | 23.7325 | 49.9173 | 1559.99
#REF! | 23.7256 | 49.8604 | 1557.01
#REF! | 23.6127 | 50.1316 | 1554.39
#REF! | 23.5591 | 50.224 | 1544.26
#REF! | 23.5293 | 50.2483 | 1538.47
#REF! | 23.5106 | 50.2446 | 1534.57
#REF! | 23.4969 | 50.2314 | 1531.66
#REF! | 23.4856 | 50.2163 | 1529.29
#REF! | 23.5323 | 50.3773 | 1527.08
#REF! | 23.5506 | 50.5877 | 1540.23
#REF! | 23.5573 | 50.7994 | 1550.16
#REF! | 23.5586 | 50.9968 | 1558.17
#REF! | 23.5576 | 51.1746 | 1564.82
#REF! | 23.5554 | 51.3321 | 1570.45
#REF! | 23.5527 | 51.4709 | 1575.26
#REF! | 23.5497 | 51.5928 | 1579.37
#REF! | 23.5464 | 51.6997 | 1582.9
#REF! | 23.543 | 51.7936 | 1585.91
#REF! | 23.5394 | 51.876 | 1588.5
#REF! | 23.5358 | 51.9485 | 1590.7
#REF! | 23.4613 | 50.4915 | 1592.81
#REF! | 23.4127 | 49.1657 | 1534.66
#REF! | 23.3783 | 47.9842 | 1485.32
#REF! | 23.3514 | 46.9449 | 1443.05
#REF! | 23.3288 | 46.037 | 1406.57
#REF! | 23.3088 | 45.2471 | 1374.97
#REF! | 23.2906 | 44.5613 | 1347.52
#REF! | 23.2737 | 43.9665 | 1323.65
#REF! | 23.258 | 43.4514 | 1302.87
#REF! | 23.2432 | 43.0056 | 1284.78
#REF! | 23.2292 | 42.62 | 1269.02
#REF! | 23.2159 | 42.2868 | 1255.27
Formulas:
Date/Time = [Date/Time, row above]+1/(24*12)